## 3-2
Analysis for IEC61000-4-7 & IEC61000-3-2/12 Harmonics Calibration & Verification protocol TR 61000-4-37 | [7 empty] | Harm . No. | Ideal | Min | Max
Mathieu van den Bergh 2013/2014/2015 | [7 empty] | 1 | 2.3534 | Tolerance
[8 empty] | 2 | 3.97e-05 | 0 | 0.012844
Change the Load resistance(s) and Start-Stop Phase as desired, then wait for the re-computation | [7 empty] | 3 | 0.91499 | 0.86924 | 0.95845
[8 empty] | 4 | 1.2067e-07 | 0 | 0.012804
|  |  |  | Calculated parameters |  |  |  | 5 | 0.30503 | 0.28978 | 0.31952
Linear load value: | 200000 | Ohm | Linear Load resistnc: |  | 200000 | Ohm |  | 6 | 3.9702e-05 | 0 | 0.012844
Contr. Load value: | 80 | Ohm |  | Contr. Load resistnc : | 80 | Ohm |  | 7 | 0.305 | 0.28975 | 0.31949
System voltage | 230 | V-rms |  | System voltage | 230 | V-rms |  | 8 | 1.2057e-07 | 0 | 0.012804
Volt-pk | 325.2691 | V-pk |  | Volt-pk | 325.2691 | V-pk |  | 9 | 0.18304 | 0.17024 | 0.19585
|  |  |  | Pwr | 541.2856 | Watts |  | 10 | 3.9706e-05 | 0 | 0.012844
|  |  |  | VA | 598.3134 |  |  | 11 | 0.18301 | 0.17021 | 0.19582
|  |  |  | PF | 0.90469 |  |  | 12 | 1.2079e-07 | 0 | 0.012804
|  |  |  | I -Cr. Fact | 1.5634 |  |  | 13 | 0.13077 | 0.11796 | 0.14357
Start Phase | Stop Phase |  |  | I - THD | 46.29% |  |  | 14 | 3.9711e-05 | 0 | 0.012844
45 | 135 | Degrees |  | I - THC | 1.0894 |  |  | 15 | 0.13074 | 0.11794 | 0.14354
0.7854 | 2.3562 | <-- Rad |  | POHC | 0.20427 |  |  | 16 | 1.2076e-07 | 0 | 0.012804
|  |  |  | Current | 2.6014 | A-rms |  | 17 | 0.10173 | 0.088928 | 0.11454
|  |  |  | Amp-pk | 4.0669 | A-pk |  | 18 | 3.9719e-05 | 0 | 0.012844
[8 empty] | 19 | 0.1017 | 0.088899 | 0.11451
|  |  |  | Start Phase | Stop Phase |  |  | 20 | 1.2103e-07 | 0 | 0.012804
|  |  |  | 45 | 135 | Degrees |  | 21 | 0.083258 | 0.070454 | 0.096063
[8 empty] | 22 | 3.9729e-05 | 0 | 0.012844
[8 empty] | 23 | 0.08323 | 0.070426 | 0.096035
phase incr. | 0.006136 | [5 empty] | Current | 24 | 1.2106e-07 | 0 | 0.012804
angle | V-t | A-t | P-t | On/Off | Ramp | On-Off | Flow | 25 | 0.070473 | 0.057669 | 0.083277
0 | 0 | 0 | 0 | FALSE | FALSE | FALSE | 0 | 26 | 3.9741e-05 | 0 | 0.012844
0.006136 | 1.9958 | 0.024944 | 1.9917e-05 | FALSE | FALSE | FALSE | 9.9791e-06 | 27 | 0.070445 | 0.057641 | 0.083249
0.012272 | 3.9916 | 0.049887 | 7.9663e-05 | FALSE | FALSE | FALSE | 1.9958e-05 | 28 | 1.214e-07 | 0 | 0.012804
0.018408 | 5.9872 | 0.074829 | 0.00017923 | FALSE | FALSE | FALSE | 2.9936e-05 | 29 | 0.0611 | 0.048296 | 0.073904
0.024544 | 7.9826 | 0.099767 | 0.0003186 | FALSE | FALSE | FALSE | 3.9913e-05 | 30 | 3.9755e-05 | 0 | 0.012844
0.03068 | 9.9777 | 0.1247 | 0.00049776 | FALSE | FALSE | FALSE | 4.9888e-05 | 31 | 0.061072 | 0.048268 | 0.073876
0.036816 | 11.9724 | 0.14963 | 0.00071668 | FALSE | FALSE | FALSE | 5.9861e-05 | 32 | 1.2149e-07 | 0 | 0.012804
0.042952 | 13.9666 | 0.17456 | 0.00097532 | FALSE | FALSE | FALSE | 6.9832e-05 | 33 | 0.053935 | 0.041131 | 0.066739
0.049088 | 15.9604 | 0.19947 | 0.0012737 | FALSE | FALSE | FALSE | 7.9801e-05 | 34 | 3.9771e-05 | 0 | 0.012844
0.055224 | 17.9535 | 0.22438 | 0.0016116 | FALSE | FALSE | FALSE | 8.9767e-05 | 35 | 0.053907 | 0.041103 | 0.066711
0.06136 | 19.9459 | 0.24929 | 0.0019892 | FALSE | FALSE | FALSE | 9.9729e-05 | 36 | 1.2188e-07 | 0 | 0.012804
0.067496 | 21.9376 | 0.27418 | 0.0024063 | FALSE | FALSE | FALSE | 0.00010969 | 37 | 0.048281 | 0.035477 | 0.061085
0.073632 | 23.9285 | 0.29906 | 0.0028628 | FALSE | FALSE | FALSE | 0.00011964 | 38 | 3.9789e-05 | 0 | 0.012844
0.079768 | 25.9185 | 0.32393 | 0.0033588 | FALSE | FALSE | FALSE | 0.00012959 | 39 | 0.048253 | 0.035449 | 0.061057
0.085904 | 27.9075 | 0.34879 | 0.0038941 | FALSE | FALSE | FALSE | 0.00013954 | 40 | 1.2203e-07 | 0 | 0.012804
0.09204 | 29.8954 | 0.37364 | 0.0044686 | FALSE | FALSE | FALSE | 0.00014948
0.098176 | 31.8823 | 0.39847 | 0.0050823 | FALSE | FALSE | FALSE | 0.00015941
0.10431 | 33.8679 | 0.42328 | 0.0057351 | FALSE | FALSE | FALSE | 0.00016934
0.11045 | 35.8522 | 0.44809 | 0.0064268 | FALSE | FALSE | FALSE | 0.00017926 |  |  |  |  | Angle |  | Limits
0.11658 | 37.8352 | 0.47287 | 0.0071575 | FALSE | FALSE | FALSE | 0.00018917 | Harm. no | Amplitude | Real | Imaginary | degrees
0.12272 | 39.8168 | 0.49763 | 0.0079268 | FALSE | FALSE | FALSE | 0.00019908 | 0 | 1.2051e-07 | 0 | -1.2051e-07 | 0 | Harm | Class-A | Class-B | Class-C | Class-D
0.12886 | 41.7969 | 0.52238 | 0.0087348 | FALSE | FALSE | FALSE | 0.00020898 | 1 | 2.3534 | 2.3534 | 0.0055582 | 0.13532
0.13499 | 43.7754 | 0.54711 | 0.0095813 | FALSE | FALSE | FALSE | 0.00021887 | 2 | 3.97e-05 | 3.9699e-05 | 2.4123e-07 | 0 | 1.5761e-09 | 1.08 | 1.62 | 0.047068 | N/A
0.14113 | 45.7522 | 0.57182 | 0.010466 | FALSE | FALSE | FALSE | 0.00022876 | 3 | 0.91499 | -0.91497 | -0.0055581 | -179.652 | 0.8372 | 2.3 | 3.45 | 0.63873 | 1.8404
0.14726 | 47.7274 | 0.5965 | 0.011389 | FALSE | FALSE | FALSE | 0.00023863 | 4 | 1.2067e-07 | 2.5173e-10 | 1.2067e-07 | 0 | 1.456e-14 | 0.43 | 0.645 | 0 | N/A
0.1534 | 49.7007 | 0.62116 | 0.012351 | FALSE | FALSE | FALSE | 0.0002485 | 5 | 0.30503 | -0.30498 | -0.0055584 | -178.9559 | 0.093043 | 1.14 | 1.71 | 0.23534 | 1.0284
0.15954 | 51.6721 | 0.6458 | 0.01335 | FALSE | FALSE | FALSE | 0.00025836 | 6 | 3.9702e-05 | -3.9695e-05 | -7.234e-07 | 0 | 1.5762e-09 | 0.3 | 0.45 | 0 | N/A
0.16567 | 53.6417 | 0.67042 | 0.014387 | FALSE | FALSE | FALSE | 0.00026821 | 7 | 0.305 | 0.30495 | 0.0055579 | 1.0441 | 0.093026 | 0.77 | 1.155 | 0.16474 | 0.54129
0.17181 | 55.6092 | 0.69501 | 0.015462 | FALSE | FALSE | FALSE | 0.00027804 | 8 | 1.2057e-07 | -5.0066e-10 | -1.2057e-07 | 0 | 1.4538e-14 | 0.23 | 0.345 | 0 | N/A
0.17794 | 57.5746 | 0.71957 | 0.016574 | FALSE | FALSE | FALSE | 0.00028787 | 9 | 0.18304 | 0.18296 | 0.0055586 | 1.7402 | 0.033504 | 0.4 | 0.6 | 0.11767 | 0.27064
0.18408 | 59.5378 | 0.74411 | 0.017724 | FALSE | FALSE | FALSE | 0.00029769 | 10 | 3.9706e-05 | 3.9687e-05 | 1.2059e-06 | 0 | 1.5765e-09 | 0.184 | 0.276 | 0 | N/A
0.19022 | 61.4988 | 0.76862 | 0.01891 | FALSE | FALSE | FALSE | 0.00030749 | 11 | 0.18301 | -0.18293 | -0.0055577 | -178.2598 | 0.033494 | 0.33 | 0.495 | 0.070603 | 0.18945
0.19635 | 63.4575 | 0.7931 | 0.020134 | FALSE | FALSE | FALSE | 0.00031728 | 12 | 1.2079e-07 | 7.5327e-10 | 1.2079e-07 | 0 | 1.459e-14 | 0.153 | 0.2295 | 0 | N/A
0.20249 | 65.4138 | 0.81755 | 0.021395 | FALSE | FALSE | FALSE | 0.00032707 | 13 | 0.13077 | -0.13065 | -0.0055588 | -177.5637 | 0.0171 | 0.21 | 0.315 | 0.070603 | 0.16022
0.20862 | 67.3676 | 0.84197 | 0.022692 | FALSE | FALSE | FALSE | 0.00033683 | 14 | 3.9711e-05 | -3.9676e-05 | -1.688e-06 | 0 | 1.577e-09 | 0.13143 | 0.19714 | 0 | N/A
0.21476 | 69.3189 | 0.86636 | 0.024025 | FALSE | FALSE | FALSE | 0.00034659 | 15 | 0.13074 | 0.13062 | 0.0055576 | 2.4363 | 0.017093 | 0.15 | 0.225 | 0.070603 | 0.13893
0.2209 | 71.2676 | 0.89071 | 0.025395 | FALSE | FALSE | FALSE | 0.00035633 | 16 | 1.2076e-07 | -9.9749e-10 | -1.2075e-07 | 0 | 1.4582e-14 | 0.115 | 0.1725 | 0 | N/A
0.22703 | 73.2135 | 0.91503 | 0.026801 | FALSE | FALSE | FALSE | 0.00036606 | 17 | 0.10173 | 0.10158 | 0.005559 | 3.1324 | 0.010349 | 0.13235 | 0.19853 | 0.070603 | 0.12259
0.23317 | 75.1568 | 0.93932 | 0.028242 | FALSE | FALSE | FALSE | 0.00037578 | 18 | 3.9719e-05 | 3.966e-05 | 2.1705e-06 | 0 | 1.5776e-09 | 0.10222 | 0.15333 | 0 | N/A
0.2393 | 77.0972 | 0.96357 | 0.02972 | FALSE | FALSE | FALSE | 0.00038548 | 19 | 0.1017 | -0.10155 | -0.0055574 | -176.8676 | 0.010344 | 0.11842 | 0.17763 | 0.070603 | 0.10968
0.24544 | 79.0347 | 0.98778 | 0.031232 | FALSE | FALSE | FALSE | 0.00039517 | 20 | 1.2103e-07 | 1.2491e-09 | 1.2103e-07 | 0 | 1.4649e-14 | 0.092 | 0.138 | 0 | N/A
0.25158 | 80.9692 | 1.012 | 0.03278 | FALSE | FALSE | FALSE | 0.00040484 | 21 | 0.083258 | -0.083073 | -0.0055592 | -176.1715 | 0.006932 | 0.10714 | 0.16071 | 0.070603 | 0.099236
0.25771 | 82.9007 | 1.0361 | 0.034362 | FALSE | FALSE | FALSE | 0.0004145 | 22 | 3.9729e-05 | -3.9641e-05 | -2.6527e-06 | 0 | 1.5784e-09 | 0.083636 | 0.12545 | 0 | N/A
0.26385 | 84.8291 | 1.0602 | 0.03598 | FALSE | FALSE | FALSE | 0.00042414 | 23 | 0.08323 | 0.083045 | 0.0055573 | 3.8285 | 0.0069273 | 0.097826 | 0.14674 | 0.070603 | 0.090606
0.26998 | 86.7543 | 1.0843 | 0.037631 | FALSE | FALSE | FALSE | 0.00043377 | 24 | 1.2106e-07 | -1.4867e-09 | -1.2105e-07 | 0 | 1.4656e-14 | 0.076667 | 0.115 | 0 | N/A
0.27612 | 88.6762 | 1.1083 | 0.039317 | FALSE | FALSE | FALSE | 0.00044338 | 25 | 0.070473 | 0.070253 | 0.0055594 | 4.5246 | 0.0049664 | 0.09 | 0.135 | 0.070603 | 0.083358
0.28226 | 90.5947 | 1.1323 | 0.041037 | FALSE | FALSE | FALSE | 0.00045297 | 26 | 3.9741e-05 | 3.9618e-05 | 3.1352e-06 | 0 | 1.5794e-09 | 0.070769 | 0.10615 | 0 | N/A
0.28839 | 92.5099 | 1.1562 | 0.04279 | FALSE | FALSE | FALSE | 0.00046254 | 27 | 0.070445 | -0.070225 | -0.0055572 | -175.4754 | 0.0049625 | 0.083333 | 0.125 | 0.070603 | 0.077183
0.29453 | 94.4215 | 1.1801 | 0.044577 | FALSE | FALSE | FALSE | 0.0004721 | 28 | 1.214e-07 | 1.7354e-09 | 1.2138e-07 | 0 | 1.4737e-14 | 0.065714 | 0.098571 | 0 | N/A
0.30066 | 96.3297 | 1.2039 | 0.046397 | FALSE | FALSE | FALSE | 0.00048164 | 29 | 0.0611 | -0.060846 | -0.0055596 | -174.7793 | 0.0037332 | 0.077586 | 0.11638 | 0.070603 | 0.07186
0.3068 | 98.2341 | 1.2277 | 0.048249 | FALSE | FALSE | FALSE | 0.00049117 | 30 | 3.9755e-05 | -3.959e-05 | -3.6174e-06 | 0 | 1.5805e-09 | 0.061333 | 0.092 | 0 | N/A
0.31294 | 100.1349 | 1.2515 | 0.050135 | FALSE | FALSE | FALSE | 0.00050067 | 31 | 0.061072 | 0.060818 | 0.005557 | 5.2207 | 0.0037298 | 0.072581 | 0.10887 | 0.070603 | 0.067224
0.31907 | 102.0319 | 1.2752 | 0.052052 | FALSE | FALSE | FALSE | 0.00051015 | 32 | 1.2149e-07 | -1.9645e-09 | -1.2147e-07 | 0 | 1.4759e-14 | 0.0575 | 0.08625 | 0 | N/A
0.32521 | 103.9251 | 1.2989 | 0.054002 | FALSE | FALSE | FALSE | 0.00051962 | 33 | 0.053935 | 0.053648 | 0.0055598 | 5.9168 | 0.002909 | 0.068182 | 0.10227 | 0.070603 | 0.06315
0.33134 | 105.8144 | 1.3225 | 0.055983 | FALSE | FALSE | FALSE | 0.00052907 | 34 | 3.9771e-05 | 3.9559e-05 | 4.0999e-06 | 0 | 1.5818e-09 | 0.054118 | 0.081176 | 0 | N/A
0.33748 | 107.6997 | 1.346 | 0.057996 | FALSE | FALSE | FALSE | 0.00053849 | 35 | 0.053907 | -0.05362 | -0.0055569 | -174.0832 | 0.0029059 | 0.064286 | 0.096429 | 0.070603 | 0.059541
0.34362 | 109.5809 | 1.3696 | 0.060039 | FALSE | FALSE | FALSE | 0.0005479 | 36 | 1.2188e-07 | 2.2084e-09 | 1.2186e-07 | 0 | 1.4856e-14 | 0.051111 | 0.076667 | 0 | N/A
0.34975 | 111.458 | 1.393 | 0.062114 | FALSE | FALSE | FALSE | 0.00055728 | 37 | 0.048281 | -0.04796 | -0.00556 | -173.3871 | 0.002331 | 0.060811 | 0.091216 | 0.070603 | 0.056323
0.35589 | 113.3309 | 1.4164 | 0.064219 | FALSE | FALSE | FALSE | 0.00056665 | 38 | 3.9789e-05 | -3.9525e-05 | -4.5821e-06 | 0 | 1.5832e-09 | 0.048421 | 0.072632 | 0 | N/A
0.36202 | 115.1995 | 1.4398 | 0.066354 | FALSE | FALSE | FALSE | 0.00057599 | 39 | 0.048253 | 0.047932 | 0.0055568 | 6.6129 | 0.0023283 | 0.057692 | 0.086538 | 0.070603 | 0.053435
0.36816 | 117.0638 | 1.4631 | 0.068519 | FALSE | FALSE | FALSE | 0.00058531 | 40 | 1.2203e-07 | -2.427e-09 | -1.2201e-07 | 0 | 1.4892e-14 | 0.046 | 0.069 | 0 | N/A
0.37429 | 118.9237 | 1.4863 | 0.070714 | FALSE | FALSE | FALSE | 0.00059461 | [5 empty] | 1.0894 | 0.20427
0.38043 | 120.7791 | 1.5095 | 0.072937 | FALSE | FALSE | FALSE | 0.00060389 | [5 empty] | THC-I | POHC
0.38657 | 122.63 | 1.5326 | 0.07519 | FALSE | FALSE | FALSE | 0.00061314
0.3927 | 124.4763 | 1.5557 | 0.077471 | FALSE | FALSE | FALSE | 0.00062238
0.39884 | 126.3178 | 1.5787 | 0.07978 | FALSE | FALSE | FALSE | 0.00063158
0.40497 | 128.1546 | 1.6017 | 0.082117 | FALSE | FALSE | FALSE | 0.00064077
0.41111 | 129.9866 | 1.6246 | 0.084482 | FALSE | FALSE | FALSE | 0.00064993
0.41725 | 131.8137 | 1.6474 | 0.086873 | FALSE | FALSE | FALSE | 0.00065906
0.42338 | 133.6358 | 1.6702 | 0.089292 | FALSE | FALSE | FALSE | 0.00066817
0.42952 | 135.4529 | 1.6929 | 0.091737 | FALSE | FALSE | FALSE | 0.00067726
0.43565 | 137.2649 | 1.7156 | 0.094207 | FALSE | FALSE | FALSE | 0.00068632
0.44179 | 139.0717 | 1.7381 | 0.096704 | FALSE | FALSE | FALSE | 0.00069535
0.44793 | 140.8733 | 1.7607 | 0.099226 | FALSE | FALSE | FALSE | 0.00070436
0.45406 | 142.6696 | 1.7831 | 0.10177 | FALSE | FALSE | FALSE | 0.00071334
0.4602 | 144.4605 | 1.8055 | 0.10434 | FALSE | FALSE | FALSE | 0.0007223
0.46633 | 146.246 | 1.8278 | 0.10694 | FALSE | FALSE | FALSE | 0.00073122
0.47247 | 148.026 | 1.85 | 0.10956 | FALSE | FALSE | FALSE | 0.00074012
0.47861 | 149.8004 | 1.8722 | 0.1122 | FALSE | FALSE | FALSE | 0.00074899
0.48474 | 151.5691 | 1.8943 | 0.11486 | FALSE | FALSE | FALSE | 0.00075784
0.49088 | 153.3322 | 1.9164 | 0.11755 | FALSE | FALSE | FALSE | 0.00076665
0.49701 | 155.0895 | 1.9383 | 0.12026 | FALSE | FALSE | FALSE | 0.00077544
0.50315 | 156.8409 | 1.9602 | 0.12299 | FALSE | FALSE | FALSE | 0.0007842
0.50929 | 158.5864 | 1.982 | 0.12575 | FALSE | FALSE | FALSE | 0.00079292
0.51542 | 160.326 | 2.0038 | 0.12852 | FALSE | FALSE | FALSE | 0.00080162
0.52156 | 162.0595 | 2.0254 | 0.13132 | FALSE | FALSE | FALSE | 0.00081029
0.52769 | 163.7869 | 2.047 | 0.13413 | FALSE | FALSE | FALSE | 0.00081893
0.53383 | 165.5082 | 2.0685 | 0.13696 | FALSE | FALSE | FALSE | 0.00082753
0.53997 | 167.2232 | 2.09 | 0.13982 | FALSE | FALSE | FALSE | 0.00083611
0.5461 | 168.9319 | 2.1113 | 0.14269 | FALSE | FALSE | FALSE | 0.00084465
0.55224 | 170.6343 | 2.1326 | 0.14558 | FALSE | FALSE | FALSE | 0.00085316
0.55837 | 172.3303 | 2.1538 | 0.14849 | FALSE | FALSE | FALSE | 0.00086164
0.56451 | 174.0197 | 2.1749 | 0.15141 | FALSE | FALSE | FALSE | 0.00087009
0.57065 | 175.7026 | 2.196 | 0.15436 | FALSE | FALSE | FALSE | 0.0008785
0.57678 | 177.3789 | 2.2169 | 0.15731 | FALSE | FALSE | FALSE | 0.00088689
0.58292 | 179.0485 | 2.2378 | 0.16029 | FALSE | FALSE | FALSE | 0.00089523
0.58905 | 180.7114 | 2.2586 | 0.16328 | FALSE | FALSE | FALSE | 0.00090355
0.59519 | 182.3675 | 2.2792 | 0.16629 | FALSE | FALSE | FALSE | 0.00091183
0.60133 | 184.0167 | 2.2999 | 0.16931 | FALSE | FALSE | FALSE | 0.00092007
0.60746 | 185.6589 | 2.3204 | 0.17234 | FALSE | FALSE | FALSE | 0.00092829
0.6136 | 187.2942 | 2.3408 | 0.17539 | FALSE | FALSE | FALSE | 0.00093646
0.61973 | 188.9224 | 2.3612 | 0.17846 | FALSE | FALSE | FALSE | 0.0009446
0.62587 | 190.5436 | 2.3814 | 0.18153 | FALSE | FALSE | FALSE | 0.00095271
0.63201 | 192.1575 | 2.4016 | 0.18462 | FALSE | FALSE | FALSE | 0.00096078
0.63814 | 193.7642 | 2.4217 | 0.18772 | FALSE | FALSE | FALSE | 0.00096881
0.64428 | 195.3636 | 2.4417 | 0.19083 | FALSE | FALSE | FALSE | 0.00097681
0.65041 | 196.9557 | 2.4616 | 0.19396 | FALSE | FALSE | FALSE | 0.00098477
0.65655 | 198.5403 | 2.4814 | 0.19709 | FALSE | FALSE | FALSE | 0.00099269
0.66269 | 200.1175 | 2.5011 | 0.20023 | FALSE | FALSE | FALSE | 0.0010006
0.66882 | 201.6871 | 2.5207 | 0.20339 | FALSE | FALSE | FALSE | 0.0010084
0.67496 | 203.2492 | 2.5402 | 0.20655 | FALSE | FALSE | FALSE | 0.0010162
0.68109 | 204.8036 | 2.5597 | 0.20972 | FALSE | FALSE | FALSE | 0.001024
0.68723 | 206.3502 | 2.579 | 0.2129 | FALSE | FALSE | FALSE | 0.0010317
0.69337 | 207.8891 | 2.5982 | 0.21609 | FALSE | FALSE | FALSE | 0.0010394
0.6995 | 209.4202 | 2.6174 | 0.21928 | FALSE | FALSE | FALSE | 0.0010471
0.70564 | 210.9434 | 2.6364 | 0.22248 | FALSE | FALSE | FALSE | 0.0010547
0.71177 | 212.4587 | 2.6553 | 0.22569 | FALSE | FALSE | FALSE | 0.0010623
0.71791 | 213.9659 | 2.6742 | 0.2289 | FALSE | FALSE | FALSE | 0.0010698
0.72405 | 215.4651 | 2.6929 | 0.23212 | FALSE | FALSE | FALSE | 0.0010773
0.73018 | 216.9562 | 2.7115 | 0.23535 | FALSE | FALSE | FALSE | 0.0010848
0.73632 | 218.4391 | 2.7301 | 0.23858 | FALSE | FALSE | FALSE | 0.0010922
0.74245 | 219.9138 | 2.7485 | 0.24181 | FALSE | FALSE | FALSE | 0.0010996
0.74859 | 221.3802 | 2.7668 | 0.24504 | FALSE | FALSE | FALSE | 0.0011069
0.75473 | 222.8383 | 2.7851 | 0.24828 | FALSE | FALSE | FALSE | 0.0011142
0.76086 | 224.288 | 2.8032 | 0.25152 | FALSE | FALSE | FALSE | 0.0011214
0.767 | 225.7292 | 2.8212 | 0.25477 | FALSE | FALSE | FALSE | 0.0011286
0.77313 | 227.162 | 2.8391 | 0.25801 | FALSE | FALSE | FALSE | 0.0011358
0.77927 | 228.5862 | 2.8569 | 0.26126 | FALSE | FALSE | FALSE | 0.0011429
0.78541 | 230.0018 | 2.8746 | 661.4248 | TRUE | FALSE | TRUE | 2.8757
0.79154 | 231.4087 | 2.8922 | 669.5414 | TRUE | FALSE | TRUE | 2.8933
0.79768 | 232.8069 | 2.9096 | 677.6569 | TRUE | FALSE | TRUE | 2.9108
0.80381 | 234.1964 | 2.927 | 685.7699 | TRUE | FALSE | TRUE | 2.9282
0.80995 | 235.577 | 2.9443 | 693.8792 | TRUE | FALSE | TRUE | 2.9454
0.81609 | 236.9487 | 2.9614 | 701.9836 | TRUE | FALSE | TRUE | 2.9626
0.82222 | 238.3116 | 2.9784 | 710.0819 | TRUE | FALSE | TRUE | 2.9796
0.82836 | 239.6655 | 2.9954 | 718.1729 | TRUE | FALSE | TRUE | 2.9966
0.83449 | 241.0103 | 3.0122 | 726.2553 | TRUE | FALSE | TRUE | 3.0134
0.84063 | 242.3461 | 3.0289 | 734.328 | TRUE | FALSE | TRUE | 3.0301
0.84677 | 243.6727 | 3.0454 | 742.3897 | TRUE | FALSE | TRUE | 3.0467
0.8529 | 244.9902 | 3.0619 | 750.4392 | TRUE | FALSE | TRUE | 3.0631
0.85904 | 246.2984 | 3.0783 | 758.4753 | TRUE | FALSE | TRUE | 3.0795
0.86517 | 247.5974 | 3.0945 | 766.4968 | TRUE | FALSE | TRUE | 3.0957
0.87131 | 248.8871 | 3.1106 | 774.5024 | TRUE | FALSE | TRUE | 3.1119
0.87745 | 250.1673 | 3.1266 | 782.491 | TRUE | FALSE | TRUE | 3.1279
0.88358 | 251.4382 | 3.1425 | 790.4614 | TRUE | FALSE | TRUE | 3.1438
0.88972 | 252.6996 | 3.1583 | 798.4124 | TRUE | FALSE | TRUE | 3.1595
0.89585 | 253.9515 | 3.1739 | 806.3427 | TRUE | FALSE | TRUE | 3.1752
0.90199 | 255.1938 | 3.1894 | 814.2512 | TRUE | FALSE | TRUE | 3.1907
0.90813 | 256.4265 | 3.2048 | 822.1367 | TRUE | FALSE | TRUE | 3.2061
0.91426 | 257.6496 | 3.2201 | 829.9979 | TRUE | FALSE | TRUE | 3.2214
0.9204 | 258.8629 | 3.2353 | 837.8338 | TRUE | FALSE | TRUE | 3.2366
0.92653 | 260.0666 | 3.2503 | 845.6431 | TRUE | FALSE | TRUE | 3.2516
0.93267 | 261.2604 | 3.2653 | 853.4247 | TRUE | FALSE | TRUE | 3.2666
0.93881 | 262.4444 | 3.2801 | 861.1774 | TRUE | FALSE | TRUE | 3.2814
0.94494 | 263.6185 | 3.2947 | 868.8999 | TRUE | FALSE | TRUE | 3.2961
0.95108 | 264.7826 | 3.3093 | 876.5912 | TRUE | FALSE | TRUE | 3.3106
0.95721 | 265.9368 | 3.3237 | 884.2502 | TRUE | FALSE | TRUE | 3.325
0.96335 | 267.081 | 3.338 | 891.8755 | TRUE | FALSE | TRUE | 3.3393
0.96949 | 268.2152 | 3.3522 | 899.4662 | TRUE | FALSE | TRUE | 3.3535
0.97562 | 269.3392 | 3.3662 | 907.021 | TRUE | FALSE | TRUE | 3.3676
0.98176 | 270.4531 | 3.3802 | 914.5388 | TRUE | FALSE | TRUE | 3.3815
0.98789 | 271.5568 | 3.3939 | 922.0185 | TRUE | FALSE | TRUE | 3.3953
0.99403 | 272.6503 | 3.4076 | 929.4589 | TRUE | FALSE | TRUE | 3.409
1.0002 | 273.7336 | 3.4212 | 936.859 | TRUE | FALSE | TRUE | 3.4225
1.0063 | 274.8065 | 3.4346 | 944.2176 | TRUE | FALSE | TRUE | 3.4359
1.0124 | 275.8691 | 3.4478 | 951.5336 | TRUE | FALSE | TRUE | 3.4492
1.0186 | 276.9213 | 3.461 | 958.8059 | TRUE | FALSE | TRUE | 3.4624
1.0247 | 277.963 | 3.474 | 966.0334 | TRUE | FALSE | TRUE | 3.4754
1.0308 | 278.9943 | 3.4869 | 973.2151 | TRUE | FALSE | TRUE | 3.4883
1.037 | 280.0151 | 3.4997 | 980.3498 | TRUE | FALSE | TRUE | 3.5011
1.0431 | 281.0254 | 3.5123 | 987.4364 | TRUE | FALSE | TRUE | 3.5137
1.0493 | 282.025 | 3.5248 | 994.474 | TRUE | FALSE | TRUE | 3.5262
1.0554 | 283.0141 | 3.5371 | 1001.4614 | TRUE | FALSE | TRUE | 3.5386
1.0615 | 283.9925 | 3.5494 | 1008.3976 | TRUE | FALSE | TRUE | 3.5508
1.0677 | 284.9602 | 3.5615 | 1015.2816 | TRUE | FALSE | TRUE | 3.5629
1.0738 | 285.9172 | 3.5734 | 1022.1122 | TRUE | FALSE | TRUE | 3.5749
1.0799 | 286.8634 | 3.5853 | 1028.8885 | TRUE | FALSE | TRUE | 3.5867
1.0861 | 287.7988 | 3.5969 | 1035.6095 | TRUE | FALSE | TRUE | 3.5984
1.0922 | 288.7234 | 3.6085 | 1042.2741 | TRUE | FALSE | TRUE | 3.6099
1.0983 | 289.6371 | 3.6199 | 1048.8814 | TRUE | FALSE | TRUE | 3.6214
1.1045 | 290.5399 | 3.6312 | 1055.4303 | TRUE | FALSE | TRUE | 3.6327
1.1106 | 291.4317 | 3.6423 | 1061.9199 | TRUE | FALSE | TRUE | 3.6438
1.1167 | 292.3126 | 3.6534 | 1068.3492 | TRUE | FALSE | TRUE | 3.6548
1.1229 | 293.1825 | 3.6642 | 1074.7172 | TRUE | FALSE | TRUE | 3.6657
1.129 | 294.0413 | 3.675 | 1081.0229 | TRUE | FALSE | TRUE | 3.6764
1.1352 | 294.8891 | 3.6856 | 1087.2655 | TRUE | FALSE | TRUE | 3.687
1.1413 | 295.7258 | 3.696 | 1093.4439 | TRUE | FALSE | TRUE | 3.6975
1.1474 | 296.5513 | 3.7063 | 1099.5572 | TRUE | FALSE | TRUE | 3.7078
1.1536 | 297.3657 | 3.7165 | 1105.6046 | TRUE | FALSE | TRUE | 3.718
1.1597 | 298.1689 | 3.7265 | 1111.5851 | TRUE | FALSE | TRUE | 3.728
1.1658 | 298.9608 | 3.7364 | 1117.4978 | TRUE | FALSE | TRUE | 3.7379
1.172 | 299.7415 | 3.7462 | 1123.3418 | TRUE | FALSE | TRUE | 3.7477
1.1781 | 300.5109 | 3.7558 | 1129.1162 | TRUE | FALSE | TRUE | 3.7573
1.1842 | 301.269 | 3.7653 | 1134.8202 | TRUE | FALSE | TRUE | 3.7668
1.1904 | 302.0158 | 3.7746 | 1140.4529 | TRUE | FALSE | TRUE | 3.7761
1.1965 | 302.7511 | 3.7838 | 1146.0134 | TRUE | FALSE | TRUE | 3.7853
1.2027 | 303.4751 | 3.7929 | 1151.501 | TRUE | FALSE | TRUE | 3.7944
1.2088 | 304.1877 | 3.8018 | 1156.9148 | TRUE | FALSE | TRUE | 3.8033
1.2149 | 304.8888 | 3.8105 | 1162.2539 | TRUE | FALSE | TRUE | 3.8121
1.2211 | 305.5784 | 3.8192 | 1167.5176 | TRUE | FALSE | TRUE | 3.8207
1.2272 | 306.2565 | 3.8276 | 1172.7051 | TRUE | FALSE | TRUE | 3.8292
1.2333 | 306.9231 | 3.836 | 1177.8156 | TRUE | FALSE | TRUE | 3.8375
1.2395 | 307.5781 | 3.8441 | 1182.8484 | TRUE | FALSE | TRUE | 3.8457
1.2456 | 308.2216 | 3.8522 | 1187.8026 | TRUE | FALSE | TRUE | 3.8537
1.2517 | 308.8534 | 3.8601 | 1192.6775 | TRUE | FALSE | TRUE | 3.8616
1.2579 | 309.4737 | 3.8678 | 1197.4724 | TRUE | FALSE | TRUE | 3.8694
1.264 | 310.0822 | 3.8754 | 1202.1866 | TRUE | FALSE | TRUE | 3.877
1.2701 | 310.6791 | 3.8829 | 1206.8194 | TRUE | FALSE | TRUE | 3.8845
1.2763 | 311.2643 | 3.8902 | 1211.37 | TRUE | FALSE | TRUE | 3.8918
1.2824 | 311.8378 | 3.8974 | 1215.8378 | TRUE | FALSE | TRUE | 3.8989
1.2886 | 312.3995 | 3.9044 | 1220.2221 | TRUE | FALSE | TRUE | 3.906
1.2947 | 312.9495 | 3.9113 | 1224.5222 | TRUE | FALSE | TRUE | 3.9128
1.3008 | 313.4877 | 3.918 | 1228.7375 | TRUE | FALSE | TRUE | 3.9196
1.307 | 314.0141 | 3.9246 | 1232.8674 | TRUE | FALSE | TRUE | 3.9262
1.3131 | 314.5286 | 3.931 | 1236.9113 | TRUE | FALSE | TRUE | 3.9326
1.3192 | 315.0314 | 3.9373 | 1240.8684 | TRUE | FALSE | TRUE | 3.9389
1.3254 | 315.5222 | 3.9434 | 1244.7383 | TRUE | FALSE | TRUE | 3.945
1.3315 | 316.0012 | 3.9494 | 1248.5204 | TRUE | FALSE | TRUE | 3.951
1.3376 | 316.4683 | 3.9553 | 1252.214 | TRUE | FALSE | TRUE | 3.9568
1.3438 | 316.9235 | 3.9609 | 1255.8187 | TRUE | FALSE | TRUE | 3.9625
1.3499 | 317.3667 | 3.9665 | 1259.3339 | TRUE | FALSE | TRUE | 3.9681
1.3561 | 317.798 | 3.9719 | 1262.759 | TRUE | FALSE | TRUE | 3.9735
1.3622 | 318.2173 | 3.9771 | 1266.0935 | TRUE | FALSE | TRUE | 3.9787
1.3683 | 318.6247 | 3.9822 | 1269.337 | TRUE | FALSE | TRUE | 3.9838
1.3745 | 319.02 | 3.9871 | 1272.4889 | TRUE | FALSE | TRUE | 3.9887
1.3806 | 319.4034 | 3.9919 | 1275.5488 | TRUE | FALSE | TRUE | 3.9935
1.3867 | 319.7747 | 3.9966 | 1278.5162 | TRUE | FALSE | TRUE | 3.9982
1.3929 | 320.1339 | 4.0011 | 1281.3907 | TRUE | FALSE | TRUE | 4.0027
1.399 | 320.4812 | 4.0054 | 1284.1718 | TRUE | FALSE | TRUE | 4.007
1.4051 | 320.8163 | 4.0096 | 1286.8591 | TRUE | FALSE | TRUE | 4.0112
1.4113 | 321.1394 | 4.0136 | 1289.4522 | TRUE | FALSE | TRUE | 4.0152
1.4174 | 321.4504 | 4.0175 | 1291.9507 | TRUE | FALSE | TRUE | 4.0191
1.4235 | 321.7492 | 4.0213 | 1294.3543 | TRUE | FALSE | TRUE | 4.0229
1.4297 | 322.036 | 4.0248 | 1296.6626 | TRUE | FALSE | TRUE | 4.0265
1.4358 | 322.3106 | 4.0283 | 1298.8752 | TRUE | FALSE | TRUE | 4.0299
1.442 | 322.5731 | 4.0316 | 1300.9918 | TRUE | FALSE | TRUE | 4.0332
1.4481 | 322.8235 | 4.0347 | 1303.0121 | TRUE | FALSE | TRUE | 4.0363
1.4542 | 323.0617 | 4.0377 | 1304.9357 | TRUE | FALSE | TRUE | 4.0393
1.4604 | 323.2878 | 4.0405 | 1306.7624 | TRUE | FALSE | TRUE | 4.0421
1.4665 | 323.5016 | 4.0432 | 1308.492 | TRUE | FALSE | TRUE | 4.0448
1.4726 | 323.7033 | 4.0457 | 1310.1241 | TRUE | FALSE | TRUE | 4.0473
1.4788 | 323.8928 | 4.048 | 1311.6585 | TRUE | FALSE | TRUE | 4.0497
1.4849 | 324.0701 | 4.0503 | 1313.095 | TRUE | FALSE | TRUE | 4.0519
1.491 | 324.2352 | 4.0523 | 1314.4333 | TRUE | FALSE | TRUE | 4.0539
1.4972 | 324.3881 | 4.0542 | 1315.6733 | TRUE | FALSE | TRUE | 4.0559
1.5033 | 324.5288 | 4.056 | 1316.8148 | TRUE | FALSE | TRUE | 4.0576
1.5095 | 324.6573 | 4.0576 | 1317.8575 | TRUE | FALSE | TRUE | 4.0592
1.5156 | 324.7735 | 4.0591 | 1318.8014 | TRUE | FALSE | TRUE | 4.0607
1.5217 | 324.8776 | 4.0604 | 1319.6463 | TRUE | FALSE | TRUE | 4.062
1.5279 | 324.9693 | 4.0615 | 1320.3921 | TRUE | FALSE | TRUE | 4.0631
1.534 | 325.0489 | 4.0625 | 1321.0386 | TRUE | FALSE | TRUE | 4.0641
1.5401 | 325.1162 | 4.0633 | 1321.5858 | TRUE | FALSE | TRUE | 4.065
1.5463 | 325.1713 | 4.064 | 1322.0336 | TRUE | FALSE | TRUE | 4.0657
1.5524 | 325.2141 | 4.0646 | 1322.3818 | TRUE | FALSE | TRUE | 4.0662
1.5585 | 325.2447 | 4.0649 | 1322.6306 | TRUE | FALSE | TRUE | 4.0666
1.5647 | 325.263 | 4.0652 | 1322.7797 | TRUE | FALSE | TRUE | 4.0668
1.5708 | 325.2691 | 4.0652 | 1322.8293 | TRUE | FALSE | TRUE | 4.0669
1.5769 | 325.263 | 4.0652 | 1322.7792 | TRUE | FALSE | TRUE | 4.0668
1.5831 | 325.2446 | 4.0649 | 1322.6296 | TRUE | FALSE | TRUE | 4.0666
1.5892 | 325.2139 | 4.0646 | 1322.3803 | TRUE | FALSE | TRUE | 4.0662
1.5954 | 325.171 | 4.064 | 1322.0316 | TRUE | FALSE | TRUE | 4.0656
1.6015 | 325.1159 | 4.0633 | 1321.5833 | TRUE | FALSE | TRUE | 4.065
1.6076 | 325.0485 | 4.0625 | 1321.0356 | TRUE | FALSE | TRUE | 4.0641
1.6138 | 324.9689 | 4.0615 | 1320.3886 | TRUE | FALSE | TRUE | 4.0631
1.6199 | 324.8771 | 4.0604 | 1319.6423 | TRUE | FALSE | TRUE | 4.062
1.626 | 324.773 | 4.059 | 1318.7969 | TRUE | FALSE | TRUE | 4.0607
1.6322 | 324.6567 | 4.0576 | 1317.8526 | TRUE | FALSE | TRUE | 4.0592
1.6383 | 324.5282 | 4.056 | 1316.8093 | TRUE | FALSE | TRUE | 4.0576
1.6444 | 324.3874 | 4.0542 | 1315.6674 | TRUE | FALSE | TRUE | 4.0559
1.6506 | 324.2344 | 4.0523 | 1314.4269 | TRUE | FALSE | TRUE | 4.0539
1.6567 | 324.0693 | 4.0503 | 1313.088 | TRUE | FALSE | TRUE | 4.0519
1.6629 | 323.8919 | 4.048 | 1311.6511 | TRUE | FALSE | TRUE | 4.0497
1.669 | 323.7023 | 4.0457 | 1310.1162 | TRUE | FALSE | TRUE | 4.0473
1.6751 | 323.5006 | 4.0431 | 1308.4836 | TRUE | FALSE | TRUE | 4.0448
1.6813 | 323.2867 | 4.0405 | 1306.7536 | TRUE | FALSE | TRUE | 4.0421
1.6874 | 323.0606 | 4.0376 | 1304.9263 | TRUE | FALSE | TRUE | 4.0393
1.6935 | 322.8223 | 4.0347 | 1303.0022 | TRUE | FALSE | TRUE | 4.0363
1.6997 | 322.5719 | 4.0315 | 1300.9814 | TRUE | FALSE | TRUE | 4.0332
1.7058 | 322.3093 | 4.0283 | 1298.8644 | TRUE | FALSE | TRUE | 4.0299
1.7119 | 322.0346 | 4.0248 | 1296.6513 | TRUE | FALSE | TRUE | 4.0264
1.7181 | 321.7478 | 4.0212 | 1294.3425 | TRUE | FALSE | TRUE | 4.0228
1.7242 | 321.4488 | 4.0175 | 1291.9385 | TRUE | FALSE | TRUE | 4.0191
1.7303 | 321.1378 | 4.0136 | 1289.4395 | TRUE | FALSE | TRUE | 4.0152
1.7365 | 320.8147 | 4.0096 | 1286.8459 | TRUE | FALSE | TRUE | 4.0112
1.7426 | 320.4794 | 4.0054 | 1284.1581 | TRUE | FALSE | TRUE | 4.007
1.7488 | 320.1322 | 4.001 | 1281.3765 | TRUE | FALSE | TRUE | 4.0026
1.7549 | 319.7728 | 3.9966 | 1278.5016 | TRUE | FALSE | TRUE | 3.9982
1.761 | 319.4015 | 3.9919 | 1275.5337 | TRUE | FALSE | TRUE | 3.9935
1.7672 | 319.0181 | 3.9871 | 1272.4734 | TRUE | FALSE | TRUE | 3.9887
1.7733 | 318.6227 | 3.9822 | 1269.321 | TRUE | FALSE | TRUE | 3.9838
1.7794 | 318.2153 | 3.9771 | 1266.077 | TRUE | FALSE | TRUE | 3.9787
1.7856 | 317.7959 | 3.9718 | 1262.7421 | TRUE | FALSE | TRUE | 3.9734
1.7917 | 317.3645 | 3.9665 | 1259.3165 | TRUE | FALSE | TRUE | 3.968
1.7978 | 316.9212 | 3.9609 | 1255.8009 | TRUE | FALSE | TRUE | 3.9625
1.804 | 316.466 | 3.9552 | 1252.1958 | TRUE | FALSE | TRUE | 3.9568
1.8101 | 315.9989 | 3.9494 | 1248.5017 | TRUE | FALSE | TRUE | 3.951
1.8163 | 315.5198 | 3.9434 | 1244.7192 | TRUE | FALSE | TRUE | 3.945
1.8224 | 315.0289 | 3.9373 | 1240.8489 | TRUE | FALSE | TRUE | 3.9388
1.8285 | 314.5261 | 3.931 | 1236.8913 | TRUE | FALSE | TRUE | 3.9326
1.8347 | 314.0115 | 3.9246 | 1232.847 | TRUE | FALSE | TRUE | 3.9261
1.8408 | 313.485 | 3.918 | 1228.7167 | TRUE | FALSE | TRUE | 3.9195
1.8469 | 312.9468 | 3.9112 | 1224.5009 | TRUE | FALSE | TRUE | 3.9128
1.8531 | 312.3967 | 3.9044 | 1220.2004 | TRUE | FALSE | TRUE | 3.9059
1.8592 | 311.835 | 3.8973 | 1215.8156 | TRUE | FALSE | TRUE | 3.8989
1.8653 | 311.2614 | 3.8902 | 1211.3474 | TRUE | FALSE | TRUE | 3.8917
1.8715 | 310.6762 | 3.8829 | 1206.7964 | TRUE | FALSE | TRUE | 3.8844
1.8776 | 310.0792 | 3.8754 | 1202.1632 | TRUE | FALSE | TRUE | 3.877
1.8837 | 309.4706 | 3.8678 | 1197.4486 | TRUE | FALSE | TRUE | 3.8693
1.8899 | 308.8503 | 3.86 | 1192.6533 | TRUE | FALSE | TRUE | 3.8616
1.896 | 308.2184 | 3.8521 | 1187.778 | TRUE | FALSE | TRUE | 3.8537
1.9022 | 307.5749 | 3.8441 | 1182.8234 | TRUE | FALSE | TRUE | 3.8456
1.9083 | 306.9198 | 3.8359 | 1177.7903 | TRUE | FALSE | TRUE | 3.8375
1.9144 | 306.2532 | 3.8276 | 1172.6794 | TRUE | FALSE | TRUE | 3.8291
1.9206 | 305.575 | 3.8191 | 1167.4915 | TRUE | FALSE | TRUE | 3.8206
1.9267 | 304.8853 | 3.8105 | 1162.2274 | TRUE | FALSE | TRUE | 3.812
1.9328 | 304.1841 | 3.8017 | 1156.8879 | TRUE | FALSE | TRUE | 3.8032
1.939 | 303.4715 | 3.7928 | 1151.4737 | TRUE | FALSE | TRUE | 3.7943
1.9451 | 302.7475 | 3.7838 | 1145.9858 | TRUE | FALSE | TRUE | 3.7853
1.9512 | 302.0121 | 3.7746 | 1140.4249 | TRUE | FALSE | TRUE | 3.7761
1.9574 | 301.2652 | 3.7652 | 1134.7918 | TRUE | FALSE | TRUE | 3.7668
1.9635 | 300.5071 | 3.7558 | 1129.0875 | TRUE | FALSE | TRUE | 3.7573
1.9697 | 299.7376 | 3.7462 | 1123.3127 | TRUE | FALSE | TRUE | 3.7477
1.9758 | 298.9569 | 3.7364 | 1117.4684 | TRUE | FALSE | TRUE | 3.7379
1.9819 | 298.1649 | 3.7265 | 1111.5553 | TRUE | FALSE | TRUE | 3.728
1.9881 | 297.3616 | 3.7165 | 1105.5745 | TRUE | FALSE | TRUE | 3.7179
1.9942 | 296.5472 | 3.7063 | 1099.5268 | TRUE | FALSE | TRUE | 3.7078
2.0003 | 295.7216 | 3.696 | 1093.4132 | TRUE | FALSE | TRUE | 3.6974
2.0065 | 294.8849 | 3.6855 | 1087.2344 | TRUE | FALSE | TRUE | 3.687
2.0126 | 294.0371 | 3.6749 | 1080.9915 | TRUE | FALSE | TRUE | 3.6764
2.0187 | 293.1782 | 3.6642 | 1074.6855 | TRUE | FALSE | TRUE | 3.6656
2.0249 | 292.3082 | 3.6533 | 1068.3172 | TRUE | FALSE | TRUE | 3.6548
2.031 | 291.4273 | 3.6423 | 1061.8876 | TRUE | FALSE | TRUE | 3.6437
2.0371 | 290.5354 | 3.6311 | 1055.3977 | TRUE | FALSE | TRUE | 3.6326
2.0433 | 289.6325 | 3.6199 | 1048.8485 | TRUE | FALSE | TRUE | 3.6213
2.0494 | 288.7188 | 3.6084 | 1042.241 | TRUE | FALSE | TRUE | 3.6099
2.0556 | 287.7941 | 3.5969 | 1035.576 | TRUE | FALSE | TRUE | 3.5983
2.0617 | 286.8587 | 3.5852 | 1028.8548 | TRUE | FALSE | TRUE | 3.5866
2.0678 | 285.9124 | 3.5734 | 1022.0782 | TRUE | FALSE | TRUE | 3.5748
2.074 | 284.9554 | 3.5614 | 1015.2473 | TRUE | FALSE | TRUE | 3.5628
2.0801 | 283.9876 | 3.5493 | 1008.3631 | TRUE | FALSE | TRUE | 3.5507
2.0862 | 283.0092 | 3.5371 | 1001.4266 | TRUE | FALSE | TRUE | 3.5385
2.0924 | 282.0201 | 3.5247 | 994.4389 | TRUE | FALSE | TRUE | 3.5261
2.0985 | 281.0203 | 3.5122 | 987.4011 | TRUE | FALSE | TRUE | 3.5136
2.1046 | 280.01 | 3.4996 | 980.3142 | TRUE | FALSE | TRUE | 3.501
2.1108 | 278.9892 | 3.4868 | 973.1793 | TRUE | FALSE | TRUE | 3.4882
2.1169 | 277.9578 | 3.4739 | 965.9974 | TRUE | FALSE | TRUE | 3.4753
2.1231 | 276.916 | 3.4609 | 958.7697 | TRUE | FALSE | TRUE | 3.4623
2.1292 | 275.8638 | 3.4478 | 951.4971 | TRUE | FALSE | TRUE | 3.4492
2.1353 | 274.8011 | 3.4345 | 944.1809 | TRUE | FALSE | TRUE | 3.4359
2.1415 | 273.7282 | 3.4211 | 936.8221 | TRUE | FALSE | TRUE | 3.4225
2.1476 | 272.6449 | 3.4075 | 929.4218 | TRUE | FALSE | TRUE | 3.4089
2.1537 | 271.5513 | 3.3939 | 921.9812 | TRUE | FALSE | TRUE | 3.3952
2.1599 | 270.4476 | 3.3801 | 914.5013 | TRUE | FALSE | TRUE | 3.3814
2.166 | 269.3336 | 3.3662 | 906.9833 | TRUE | FALSE | TRUE | 3.3675
2.1721 | 268.2095 | 3.3521 | 899.4283 | TRUE | FALSE | TRUE | 3.3535
2.1783 | 267.0753 | 3.3379 | 891.8375 | TRUE | FALSE | TRUE | 3.3393
2.1844 | 265.9311 | 3.3236 | 884.212 | TRUE | FALSE | TRUE | 3.325
2.1905 | 264.7768 | 3.3092 | 876.5529 | TRUE | FALSE | TRUE | 3.3105
2.1967 | 263.6126 | 3.2947 | 868.8614 | TRUE | FALSE | TRUE | 3.296
2.2028 | 262.4385 | 3.28 | 861.1387 | TRUE | FALSE | TRUE | 3.2813
2.209 | 261.2544 | 3.2652 | 853.3859 | TRUE | FALSE | TRUE | 3.2665
2.2151 | 260.0606 | 3.2503 | 845.6042 | TRUE | FALSE | TRUE | 3.2516
2.2212 | 258.8569 | 3.2352 | 837.7947 | TRUE | FALSE | TRUE | 3.2365
2.2274 | 257.6435 | 3.2201 | 829.9587 | TRUE | FALSE | TRUE | 3.2213
2.2335 | 256.4204 | 3.2048 | 822.0973 | TRUE | FALSE | TRUE | 3.2061
2.2396 | 255.1876 | 3.1894 | 814.2117 | TRUE | FALSE | TRUE | 3.1906
2.2458 | 253.9453 | 3.1738 | 806.3031 | TRUE | FALSE | TRUE | 3.1751
2.2519 | 252.6933 | 3.1582 | 798.3727 | TRUE | FALSE | TRUE | 3.1595
2.258 | 251.4319 | 3.1424 | 790.4216 | TRUE | FALSE | TRUE | 3.1437
2.2642 | 250.161 | 3.1265 | 782.4511 | TRUE | FALSE | TRUE | 3.1278
2.2703 | 248.8806 | 3.1105 | 774.4624 | TRUE | FALSE | TRUE | 3.1118
2.2764 | 247.5909 | 3.0944 | 766.4567 | TRUE | FALSE | TRUE | 3.0957
2.2826 | 246.2919 | 3.0782 | 758.4352 | TRUE | FALSE | TRUE | 3.0794
2.2887 | 244.9836 | 3.0618 | 750.399 | TRUE | FALSE | TRUE | 3.0631
2.2949 | 243.6661 | 3.0454 | 742.3494 | TRUE | FALSE | TRUE | 3.0466
2.301 | 242.3394 | 3.0288 | 734.2877 | TRUE | FALSE | TRUE | 3.03
2.3071 | 241.0036 | 3.0121 | 726.215 | TRUE | FALSE | TRUE | 3.0133
2.3133 | 239.6587 | 2.9953 | 718.1325 | TRUE | FALSE | TRUE | 2.9965
2.3194 | 238.3048 | 2.9784 | 710.0414 | TRUE | FALSE | TRUE | 2.9796
2.3255 | 236.9419 | 2.9613 | 701.9431 | TRUE | FALSE | TRUE | 2.9625
2.3317 | 235.5701 | 2.9442 | 693.8386 | TRUE | FALSE | TRUE | 2.9454
2.3378 | 234.1894 | 2.9269 | 685.7293 | TRUE | FALSE | TRUE | 2.9281
2.3439 | 232.7999 | 2.9096 | 677.6163 | TRUE | FALSE | TRUE | 2.9107
2.3501 | 231.4017 | 2.8921 | 669.5009 | TRUE | FALSE | TRUE | 2.8932
2.3562 | 229.9947 | 2.8745 | 0.26449 | FALSE | FALSE | FALSE | 0.00115
2.3624 | 228.5791 | 2.8568 | 0.26124 | FALSE | FALSE | FALSE | 0.0011429
2.3685 | 227.1548 | 2.839 | 0.25799 | FALSE | FALSE | FALSE | 0.0011358
2.3746 | 225.7221 | 2.8211 | 0.25475 | FALSE | FALSE | FALSE | 0.0011286
2.3808 | 224.2808 | 2.8031 | 0.25151 | FALSE | FALSE | FALSE | 0.0011214
2.3869 | 222.831 | 2.785 | 0.24827 | FALSE | FALSE | FALSE | 0.0011141
2.393 | 221.3729 | 2.7667 | 0.24503 | FALSE | FALSE | FALSE | 0.0011069
2.3992 | 219.9065 | 2.7484 | 0.24179 | FALSE | FALSE | FALSE | 0.0010995
2.4053 | 218.4317 | 2.73 | 0.23856 | FALSE | FALSE | FALSE | 0.0010921
2.4114 | 216.9488 | 2.7115 | 0.23533 | FALSE | FALSE | FALSE | 0.0010847
2.4176 | 215.4576 | 2.6928 | 0.23211 | FALSE | FALSE | FALSE | 0.0010773
2.4237 | 213.9584 | 2.6741 | 0.22889 | FALSE | FALSE | FALSE | 0.0010698
2.4298 | 212.4511 | 2.6552 | 0.22568 | FALSE | FALSE | FALSE | 0.0010622
2.436 | 210.9358 | 2.6363 | 0.22247 | FALSE | FALSE | FALSE | 0.0010547
2.4421 | 209.4126 | 2.6173 | 0.21927 | FALSE | FALSE | FALSE | 0.0010471
2.4483 | 207.8815 | 2.5981 | 0.21607 | FALSE | FALSE | FALSE | 0.0010394
2.4544 | 206.3425 | 2.5789 | 0.21288 | FALSE | FALSE | FALSE | 0.0010317
2.4605 | 204.7958 | 2.5596 | 0.2097 | FALSE | FALSE | FALSE | 0.001024
2.4667 | 203.2414 | 2.5401 | 0.20653 | FALSE | FALSE | FALSE | 0.0010162
2.4728 | 201.6793 | 2.5206 | 0.20337 | FALSE | FALSE | FALSE | 0.0010084
2.4789 | 200.1096 | 2.501 | 0.20022 | FALSE | FALSE | FALSE | 0.0010005
2.4851 | 198.5324 | 2.4813 | 0.19707 | FALSE | FALSE | FALSE | 0.00099265
2.4912 | 196.9477 | 2.4615 | 0.19394 | FALSE | FALSE | FALSE | 0.00098473
2.4973 | 195.3557 | 2.4416 | 0.19082 | FALSE | FALSE | FALSE | 0.00097677
2.5035 | 193.7562 | 2.4216 | 0.18771 | FALSE | FALSE | FALSE | 0.00096877
2.5096 | 192.1495 | 2.4015 | 0.18461 | FALSE | FALSE | FALSE | 0.00096074
2.5158 | 190.5355 | 2.3813 | 0.18152 | FALSE | FALSE | FALSE | 0.00095267
2.5219 | 188.9143 | 2.3611 | 0.17844 | FALSE | FALSE | FALSE | 0.00094456
2.528 | 187.2861 | 2.3407 | 0.17538 | FALSE | FALSE | FALSE | 0.00093642
2.5342 | 185.6507 | 2.3203 | 0.17233 | FALSE | FALSE | FALSE | 0.00092824
2.5403 | 184.0084 | 2.2998 | 0.16929 | FALSE | FALSE | FALSE | 0.00092003
2.5464 | 182.3592 | 2.2791 | 0.16627 | FALSE | FALSE | FALSE | 0.00091179
2.5526 | 180.7031 | 2.2584 | 0.16327 | FALSE | FALSE | FALSE | 0.00090351
2.5587 | 179.0402 | 2.2377 | 0.16028 | FALSE | FALSE | FALSE | 0.00089519
2.5648 | 177.3705 | 2.2168 | 0.1573 | FALSE | FALSE | FALSE | 0.00088684
2.571 | 175.6942 | 2.1958 | 0.15434 | FALSE | FALSE | FALSE | 0.00087846
2.5771 | 174.0113 | 2.1748 | 0.1514 | FALSE | FALSE | FALSE | 0.00087005
2.5832 | 172.3218 | 2.1537 | 0.14847 | FALSE | FALSE | FALSE | 0.0008616
2.5894 | 170.6258 | 2.1325 | 0.14556 | FALSE | FALSE | FALSE | 0.00085312
2.5955 | 168.9234 | 2.1112 | 0.14267 | FALSE | FALSE | FALSE | 0.00084461
2.6017 | 167.2147 | 2.0899 | 0.1398 | FALSE | FALSE | FALSE | 0.00083607
2.6078 | 165.4996 | 2.0684 | 0.13695 | FALSE | FALSE | FALSE | 0.00082749
2.6139 | 163.7783 | 2.0469 | 0.13412 | FALSE | FALSE | FALSE | 0.00081888
2.6201 | 162.0509 | 2.0253 | 0.1313 | FALSE | FALSE | FALSE | 0.00081025
2.6262 | 160.3173 | 2.0037 | 0.12851 | FALSE | FALSE | FALSE | 0.00080158
2.6323 | 158.5777 | 1.9819 | 0.12573 | FALSE | FALSE | FALSE | 0.00079288
2.6385 | 156.8321 | 1.9601 | 0.12298 | FALSE | FALSE | FALSE | 0.00078415
2.6446 | 155.0807 | 1.9382 | 0.12025 | FALSE | FALSE | FALSE | 0.0007754
2.6507 | 153.3234 | 1.9163 | 0.11754 | FALSE | FALSE | FALSE | 0.00076661
2.6569 | 151.5603 | 1.8942 | 0.11485 | FALSE | FALSE | FALSE | 0.00075779
2.663 | 149.7915 | 1.8721 | 0.11219 | FALSE | FALSE | FALSE | 0.00074895
2.6692 | 148.0171 | 1.8499 | 0.10954 | FALSE | FALSE | FALSE | 0.00074008
2.6753 | 146.2371 | 1.8277 | 0.10693 | FALSE | FALSE | FALSE | 0.00073118
2.6814 | 144.4516 | 1.8054 | 0.10433 | FALSE | FALSE | FALSE | 0.00072225
2.6876 | 142.6606 | 1.783 | 0.10176 | FALSE | FALSE | FALSE | 0.0007133
2.6937 | 140.8643 | 1.7605 | 0.099213 | FALSE | FALSE | FALSE | 0.00070431
2.6998 | 139.0627 | 1.738 | 0.096691 | FALSE | FALSE | FALSE | 0.00069531
2.706 | 137.2559 | 1.7154 | 0.094195 | FALSE | FALSE | FALSE | 0.00068627
2.7121 | 135.4438 | 1.6928 | 0.091724 | FALSE | FALSE | FALSE | 0.00067721
2.7182 | 133.6267 | 1.6701 | 0.08928 | FALSE | FALSE | FALSE | 0.00066813
2.7244 | 131.8046 | 1.6473 | 0.086861 | FALSE | FALSE | FALSE | 0.00065902
2.7305 | 129.9775 | 1.6245 | 0.08447 | FALSE | FALSE | FALSE | 0.00064988
2.7366 | 128.1455 | 1.6016 | 0.082105 | FALSE | FALSE | FALSE | 0.00064072
2.7428 | 126.3086 | 1.5786 | 0.079769 | FALSE | FALSE | FALSE | 0.00063154
2.7489 | 124.467 | 1.5556 | 0.077459 | FALSE | FALSE | FALSE | 0.00062233
2.7551 | 122.6208 | 1.5325 | 0.075179 | FALSE | FALSE | FALSE | 0.0006131
2.7612 | 120.7699 | 1.5094 | 0.072926 | FALSE | FALSE | FALSE | 0.00060384
2.7673 | 118.9144 | 1.4862 | 0.070703 | FALSE | FALSE | FALSE | 0.00059457
2.7735 | 117.0545 | 1.463 | 0.068508 | FALSE | FALSE | FALSE | 0.00058527
2.7796 | 115.1902 | 1.4397 | 0.066343 | FALSE | FALSE | FALSE | 0.00057595
2.7857 | 113.3215 | 1.4163 | 0.064208 | FALSE | FALSE | FALSE | 0.0005666
2.7919 | 111.4486 | 1.3929 | 0.062103 | FALSE | FALSE | FALSE | 0.00055724
2.798 | 109.5715 | 1.3694 | 0.060029 | FALSE | FALSE | FALSE | 0.00054785
2.8041 | 107.6903 | 1.3459 | 0.057985 | FALSE | FALSE | FALSE | 0.00053845
2.8103 | 105.805 | 1.3224 | 0.055973 | FALSE | FALSE | FALSE | 0.00052902
2.8164 | 103.9157 | 1.2987 | 0.053992 | FALSE | FALSE | FALSE | 0.00051957
2.8226 | 102.0225 | 1.2751 | 0.052042 | FALSE | FALSE | FALSE | 0.00051011
2.8287 | 100.1254 | 1.2514 | 0.050125 | FALSE | FALSE | FALSE | 0.00050062
2.8348 | 98.2246 | 1.2276 | 0.04824 | FALSE | FALSE | FALSE | 0.00049112
2.841 | 96.3201 | 1.2038 | 0.046387 | FALSE | FALSE | FALSE | 0.0004816
2.8471 | 94.412 | 1.18 | 0.044568 | FALSE | FALSE | FALSE | 0.00047206
2.8532 | 92.5003 | 1.1561 | 0.042781 | FALSE | FALSE | FALSE | 0.0004625
2.8594 | 90.5851 | 1.1321 | 0.041028 | FALSE | FALSE | FALSE | 0.00045292
2.8655 | 88.6666 | 1.1082 | 0.039308 | FALSE | FALSE | FALSE | 0.00044333
2.8716 | 86.7446 | 1.0841 | 0.037623 | FALSE | FALSE | FALSE | 0.00043372
2.8778 | 84.8194 | 1.0601 | 0.035971 | FALSE | FALSE | FALSE | 0.00042409
2.8839 | 82.8911 | 1.036 | 0.034354 | FALSE | FALSE | FALSE | 0.00041445
2.89 | 80.9596 | 1.0118 | 0.032772 | FALSE | FALSE | FALSE | 0.00040479
2.8962 | 79.025 | 0.98766 | 0.031224 | FALSE | FALSE | FALSE | 0.00039512
2.9023 | 77.0875 | 0.96345 | 0.029712 | FALSE | FALSE | FALSE | 0.00038543
2.9085 | 75.1471 | 0.9392 | 0.028235 | FALSE | FALSE | FALSE | 0.00037573
2.9146 | 73.2038 | 0.91491 | 0.026794 | FALSE | FALSE | FALSE | 0.00036602
2.9207 | 71.2578 | 0.89059 | 0.025388 | FALSE | FALSE | FALSE | 0.00035629
2.9269 | 69.3091 | 0.86623 | 0.024019 | FALSE | FALSE | FALSE | 0.00034654
2.933 | 67.3578 | 0.84185 | 0.022685 | FALSE | FALSE | FALSE | 0.00033679
2.9391 | 65.404 | 0.81743 | 0.021388 | FALSE | FALSE | FALSE | 0.00032702
2.9453 | 63.4477 | 0.79298 | 0.020128 | FALSE | FALSE | FALSE | 0.00031724
2.9514 | 61.489 | 0.7685 | 0.018904 | FALSE | FALSE | FALSE | 0.00030744
2.9575 | 59.528 | 0.74399 | 0.017718 | FALSE | FALSE | FALSE | 0.00029764
2.9637 | 57.5647 | 0.71945 | 0.016568 | FALSE | FALSE | FALSE | 0.00028782
2.9698 | 55.5993 | 0.69489 | 0.015456 | FALSE | FALSE | FALSE | 0.00027799
2.976 | 53.6318 | 0.6703 | 0.014382 | FALSE | FALSE | FALSE | 0.00026816
2.9821 | 51.6623 | 0.64568 | 0.013345 | FALSE | FALSE | FALSE | 0.00025831
2.9882 | 49.6908 | 0.62104 | 0.012346 | FALSE | FALSE | FALSE | 0.00024845
2.9944 | 47.7175 | 0.59638 | 0.011385 | FALSE | FALSE | FALSE | 0.00023859
3.0005 | 45.7423 | 0.57169 | 0.010462 | FALSE | FALSE | FALSE | 0.00022871
3.0066 | 43.7655 | 0.54699 | 0.009577 | FALSE | FALSE | FALSE | 0.00021883
3.0128 | 41.787 | 0.52226 | 0.0087307 | FALSE | FALSE | FALSE | 0.00020893
3.0189 | 39.8069 | 0.49751 | 0.0079229 | FALSE | FALSE | FALSE | 0.00019903
3.025 | 37.8253 | 0.47275 | 0.0071537 | FALSE | FALSE | FALSE | 0.00018912
3.0312 | 35.8423 | 0.44796 | 0.0064233 | FALSE | FALSE | FALSE | 0.00017921
3.0373 | 33.858 | 0.42316 | 0.0057318 | FALSE | FALSE | FALSE | 0.00016929
3.0434 | 31.8723 | 0.39834 | 0.0050792 | FALSE | FALSE | FALSE | 0.00015936
3.0496 | 29.8855 | 0.37351 | 0.0044657 | FALSE | FALSE | FALSE | 0.00014943
3.0557 | 27.8975 | 0.34867 | 0.0038913 | FALSE | FALSE | FALSE | 0.00013949
3.0619 | 25.9085 | 0.32381 | 0.0033562 | FALSE | FALSE | FALSE | 0.00012954
3.068 | 23.9186 | 0.29894 | 0.0028605 | FALSE | FALSE | FALSE | 0.00011959
3.0741 | 21.9277 | 0.27405 | 0.0024041 | FALSE | FALSE | FALSE | 0.00010964
3.0803 | 19.936 | 0.24916 | 0.0019872 | FALSE | FALSE | FALSE | 9.9679e-05
3.0864 | 17.9435 | 0.22426 | 0.0016098 | FALSE | FALSE | FALSE | 8.9717e-05
3.0925 | 15.9504 | 0.19935 | 0.0012721 | FALSE | FALSE | FALSE | 7.9751e-05
3.0987 | 13.9567 | 0.17443 | 0.00097393 | FALSE | FALSE | FALSE | 6.9783e-05
3.1048 | 11.9624 | 0.14951 | 0.00071549 | FALSE | FALSE | FALSE | 5.9811e-05
3.1109 | 9.9677 | 0.12458 | 0.00049677 | FALSE | FALSE | FALSE | 4.9838e-05
3.1171 | 7.9726 | 0.099643 | 0.00031781 | FALSE | FALSE | FALSE | 3.9863e-05
3.1232 | 5.9772 | 0.074704 | 0.00017863 | FALSE | FALSE | FALSE | 2.9886e-05
3.1294 | 3.9816 | 0.049763 | 7.9265e-05 | FALSE | FALSE | FALSE | 1.9908e-05
3.1355 | 1.9859 | 0.024819 | 1.9718e-05 | FALSE | FALSE | FALSE | 9.9292e-06
3.1416 | -0.0099792 | -0.00012472 | 4.9792e-10 | FALSE | FALSE | FALSE | -4.9896e-08
3.1478 | -2.0058 | -0.025069 | 2.0116e-05 | FALSE | FALSE | FALSE | -1.0029e-05
3.1539 | -4.0016 | -0.050012 | 8.0062e-05 | FALSE | FALSE | FALSE | -2.0008e-05
3.16 | -5.9972 | -0.074953 | 0.00017983 | FALSE | FALSE | FALSE | -2.9986e-05
3.1662 | -7.9926 | -0.099892 | 0.0003194 | FALSE | FALSE | FALSE | -3.9962e-05
3.1723 | -9.9876 | -0.12483 | 0.00049876 | FALSE | FALSE | FALSE | -4.9938e-05
3.1784 | -11.9823 | -0.14976 | 0.00071788 | FALSE | FALSE | FALSE | -5.9911e-05
3.1846 | -13.9766 | -0.17468 | 0.00097672 | FALSE | FALSE | FALSE | -6.9882e-05
3.1907 | -15.9703 | -0.1996 | 0.0012752 | FALSE | FALSE | FALSE | -7.9851e-05
3.1968 | -17.9634 | -0.22451 | 0.0016134 | FALSE | FALSE | FALSE | -8.9816e-05
3.203 | -19.9559 | -0.24941 | 0.0019912 | FALSE | FALSE | FALSE | -9.9779e-05
3.2091 | -21.9476 | -0.2743 | 0.0024085 | FALSE | FALSE | FALSE | -0.00010974
3.2153 | -23.9385 | -0.29919 | 0.0028652 | FALSE | FALSE | FALSE | -0.00011969
3.2214 | -25.9284 | -0.32406 | 0.0033614 | FALSE | FALSE | FALSE | -0.00012964
3.2275 | -27.9174 | -0.34892 | 0.0038969 | FALSE | FALSE | FALSE | -0.00013959
3.2337 | -29.9054 | -0.37376 | 0.0044716 | FALSE | FALSE | FALSE | -0.00014953
3.2398 | -31.8922 | -0.39859 | 0.0050855 | FALSE | FALSE | FALSE | -0.00015946
3.2459 | -33.8778 | -0.42341 | 0.0057385 | FALSE | FALSE | FALSE | -0.00016939
3.2521 | -35.8621 | -0.44821 | 0.0064304 | FALSE | FALSE | FALSE | -0.00017931
3.2582 | -37.8451 | -0.47299 | 0.0071612 | FALSE | FALSE | FALSE | -0.00018922
3.2643 | -39.8267 | -0.49776 | 0.0079308 | FALSE | FALSE | FALSE | -0.00019913
3.2705 | -41.8068 | -0.52251 | 0.0087389 | FALSE | FALSE | FALSE | -0.00020903
3.2766 | -43.7853 | -0.54723 | 0.0095857 | FALSE | FALSE | FALSE | -0.00021892
3.2828 | -45.7621 | -0.57194 | 0.010471 | FALSE | FALSE | FALSE | -0.00022881
3.2889 | -47.7372 | -0.59663 | 0.011394 | FALSE | FALSE | FALSE | -0.00023868
3.295 | -49.7105 | -0.62129 | 0.012356 | FALSE | FALSE | FALSE | -0.00024855
3.3012 | -51.682 | -0.64593 | 0.013355 | FALSE | FALSE | FALSE | -0.00025841
3.3073 | -53.6515 | -0.67054 | 0.014392 | FALSE | FALSE | FALSE | -0.00026825
3.3134 | -55.619 | -0.69513 | 0.015467 | FALSE | FALSE | FALSE | -0.00027809
3.3196 | -57.5844 | -0.7197 | 0.01658 | FALSE | FALSE | FALSE | -0.00028792
3.3257 | -59.5476 | -0.74423 | 0.017729 | FALSE | FALSE | FALSE | -0.00029774
3.3318 | -61.5086 | -0.76874 | 0.018916 | FALSE | FALSE | FALSE | -0.00030754
3.338 | -63.4673 | -0.79322 | 0.02014 | FALSE | FALSE | FALSE | -0.00031733
3.3441 | -65.4235 | -0.81767 | 0.021401 | FALSE | FALSE | FALSE | -0.00032711
3.3502 | -67.3773 | -0.84209 | 0.022698 | FALSE | FALSE | FALSE | -0.00033688
3.3564 | -69.3286 | -0.86648 | 0.024032 | FALSE | FALSE | FALSE | -0.00034664
3.3625 | -71.2773 | -0.89083 | 0.025402 | FALSE | FALSE | FALSE | -0.00035638
3.3687 | -73.2233 | -0.91515 | 0.026808 | FALSE | FALSE | FALSE | -0.00036611
3.3748 | -75.1665 | -0.93944 | 0.02825 | FALSE | FALSE | FALSE | -0.00037583
3.3809 | -77.1069 | -0.96369 | 0.029727 | FALSE | FALSE | FALSE | -0.00038553
3.3871 | -79.0444 | -0.98791 | 0.03124 | FALSE | FALSE | FALSE | -0.00039522
3.3932 | -80.9789 | -1.0121 | 0.032788 | FALSE | FALSE | FALSE | -0.00040489
3.3993 | -82.9104 | -1.0362 | 0.03437 | FALSE | FALSE | FALSE | -0.00041455
3.4055 | -84.8387 | -1.0603 | 0.035988 | FALSE | FALSE | FALSE | -0.00042419
3.4116 | -86.7639 | -1.0844 | 0.037639 | FALSE | FALSE | FALSE | -0.00043382
3.4177 | -88.6858 | -1.1084 | 0.039325 | FALSE | FALSE | FALSE | -0.00044342
3.4239 | -90.6043 | -1.1324 | 0.041045 | FALSE | FALSE | FALSE | -0.00045302
3.43 | -92.5194 | -1.1563 | 0.042799 | FALSE | FALSE | FALSE | -0.00046259
3.4362 | -94.4311 | -1.1802 | 0.044586 | FALSE | FALSE | FALSE | -0.00047215
3.4423 | -96.3392 | -1.2041 | 0.046406 | FALSE | FALSE | FALSE | -0.00048169
3.4484 | -98.2437 | -1.2279 | 0.048259 | FALSE | FALSE | FALSE | -0.00049121
3.4546 | -100.1444 | -1.2516 | 0.050144 | FALSE | FALSE | FALSE | -0.00050072
3.4607 | -102.0414 | -1.2753 | 0.052062 | FALSE | FALSE | FALSE | -0.0005102
3.4668 | -103.9346 | -1.299 | 0.054011 | FALSE | FALSE | FALSE | -0.00051967
3.473 | -105.8238 | -1.3226 | 0.055993 | FALSE | FALSE | FALSE | -0.00052911
3.4791 | -107.7091 | -1.3462 | 0.058006 | FALSE | FALSE | FALSE | -0.00053854
3.4852 | -109.5903 | -1.3697 | 0.06005 | FALSE | FALSE | FALSE | -0.00054795
3.4914 | -111.4674 | -1.3931 | 0.062124 | FALSE | FALSE | FALSE | -0.00055733
3.4975 | -113.3403 | -1.4165 | 0.064229 | FALSE | FALSE | FALSE | -0.0005667
3.5036 | -115.2089 | -1.4399 | 0.066365 | FALSE | FALSE | FALSE | -0.00057604
3.5098 | -117.0731 | -1.4632 | 0.06853 | FALSE | FALSE | FALSE | -0.00058536
3.5159 | -118.933 | -1.4864 | 0.070725 | FALSE | FALSE | FALSE | -0.00059466
3.5221 | -120.7884 | -1.5096 | 0.072948 | FALSE | FALSE | FALSE | -0.00060394
3.5282 | -122.6392 | -1.5328 | 0.075201 | FALSE | FALSE | FALSE | -0.00061319
3.5343 | -124.4855 | -1.5558 | 0.077482 | FALSE | FALSE | FALSE | -0.00062242
3.5405 | -126.327 | -1.5788 | 0.079792 | FALSE | FALSE | FALSE | -0.00063163
3.5466 | -128.1638 | -1.6018 | 0.082129 | FALSE | FALSE | FALSE | -0.00064081
3.5527 | -129.9958 | -1.6247 | 0.084494 | FALSE | FALSE | FALSE | -0.00064997
3.5589 | -131.8228 | -1.6475 | 0.086885 | FALSE | FALSE | FALSE | -0.00065911
3.565 | -133.6449 | -1.6703 | 0.089304 | FALSE | FALSE | FALSE | -0.00066822
3.5711 | -135.462 | -1.693 | 0.091749 | FALSE | FALSE | FALSE | -0.0006773
3.5773 | -137.274 | -1.7157 | 0.09422 | FALSE | FALSE | FALSE | -0.00068636
3.5834 | -139.0808 | -1.7382 | 0.096716 | FALSE | FALSE | FALSE | -0.0006954
3.5896 | -140.8823 | -1.7608 | 0.099238 | FALSE | FALSE | FALSE | -0.0007044
3.5957 | -142.6786 | -1.7832 | 0.10178 | FALSE | FALSE | FALSE | -0.00071339
3.6018 | -144.4695 | -1.8056 | 0.10436 | FALSE | FALSE | FALSE | -0.00072234
3.608 | -146.2549 | -1.8279 | 0.10695 | FALSE | FALSE | FALSE | -0.00073127
3.6141 | -148.0349 | -1.8502 | 0.10957 | FALSE | FALSE | FALSE | -0.00074017
3.6202 | -149.8092 | -1.8723 | 0.11221 | FALSE | FALSE | FALSE | -0.00074904
3.6264 | -151.578 | -1.8944 | 0.11488 | FALSE | FALSE | FALSE | -0.00075788
3.6325 | -153.341 | -1.9165 | 0.11757 | FALSE | FALSE | FALSE | -0.0007667
3.6386 | -155.0982 | -1.9384 | 0.12028 | FALSE | FALSE | FALSE | -0.00077548
3.6448 | -156.8496 | -1.9603 | 0.12301 | FALSE | FALSE | FALSE | -0.00078424
3.6509 | -158.5951 | -1.9821 | 0.12576 | FALSE | FALSE | FALSE | -0.00079297
3.657 | -160.3347 | -2.0039 | 0.12853 | FALSE | FALSE | FALSE | -0.00080167
3.6632 | -162.0682 | -2.0255 | 0.13133 | FALSE | FALSE | FALSE | -0.00081033
3.6693 | -163.7956 | -2.0471 | 0.13414 | FALSE | FALSE | FALSE | -0.00081897
3.6755 | -165.5168 | -2.0686 | 0.13698 | FALSE | FALSE | FALSE | -0.00082758
3.6816 | -167.2318 | -2.0901 | 0.13983 | FALSE | FALSE | FALSE | -0.00083615
3.6877 | -168.9405 | -2.1114 | 0.1427 | FALSE | FALSE | FALSE | -0.00084469
3.6939 | -170.6428 | -2.1327 | 0.14559 | FALSE | FALSE | FALSE | -0.00085321
3.7 | -172.3387 | -2.1539 | 0.1485 | FALSE | FALSE | FALSE | -0.00086169
3.7061 | -174.0282 | -2.175 | 0.15143 | FALSE | FALSE | FALSE | -0.00087013
3.7123 | -175.711 | -2.1961 | 0.15437 | FALSE | FALSE | FALSE | -0.00087855
3.7184 | -177.3873 | -2.217 | 0.15733 | FALSE | FALSE | FALSE | -0.00088693
3.7245 | -179.0569 | -2.2379 | 0.16031 | FALSE | FALSE | FALSE | -0.00089528
3.7307 | -180.7197 | -2.2587 | 0.1633 | FALSE | FALSE | FALSE | -0.00090359
3.7368 | -182.3757 | -2.2794 | 0.1663 | FALSE | FALSE | FALSE | -0.00091187
3.7429 | -184.0249 | -2.3 | 0.16932 | FALSE | FALSE | FALSE | -0.00092012
3.7491 | -185.6671 | -2.3205 | 0.17236 | FALSE | FALSE | FALSE | -0.00092833
3.7552 | -187.3024 | -2.3409 | 0.17541 | FALSE | FALSE | FALSE | -0.0009365
3.7614 | -188.9306 | -2.3613 | 0.17847 | FALSE | FALSE | FALSE | -0.00094464
3.7675 | -190.5517 | -2.3815 | 0.18155 | FALSE | FALSE | FALSE | -0.00095275
3.7736 | -192.1656 | -2.4017 | 0.18464 | FALSE | FALSE | FALSE | -0.00096082
3.7798 | -193.7722 | -2.4218 | 0.18774 | FALSE | FALSE | FALSE | -0.00096885
3.7859 | -195.3716 | -2.4418 | 0.19085 | FALSE | FALSE | FALSE | -0.00097685
3.792 | -196.9636 | -2.4617 | 0.19397 | FALSE | FALSE | FALSE | -0.00098481
3.7982 | -198.5482 | -2.4815 | 0.19711 | FALSE | FALSE | FALSE | -0.00099273
3.8043 | -200.1254 | -2.5012 | 0.20025 | FALSE | FALSE | FALSE | -0.0010006
3.8104 | -201.695 | -2.5208 | 0.2034 | FALSE | FALSE | FALSE | -0.0010085
3.8166 | -203.257 | -2.5403 | 0.20656 | FALSE | FALSE | FALSE | -0.0010163
3.8227 | -204.8113 | -2.5598 | 0.20974 | FALSE | FALSE | FALSE | -0.001024
3.8289 | -206.3579 | -2.5791 | 0.21292 | FALSE | FALSE | FALSE | -0.0010318
3.835 | -207.8968 | -2.5983 | 0.2161 | FALSE | FALSE | FALSE | -0.0010395
3.8411 | -209.4279 | -2.6175 | 0.2193 | FALSE | FALSE | FALSE | -0.0010471
3.8473 | -210.951 | -2.6365 | 0.2225 | FALSE | FALSE | FALSE | -0.0010547
3.8534 | -212.4662 | -2.6554 | 0.22571 | FALSE | FALSE | FALSE | -0.0010623
3.8595 | -213.9734 | -2.6743 | 0.22892 | FALSE | FALSE | FALSE | -0.0010699
3.8657 | -215.4726 | -2.693 | 0.23214 | FALSE | FALSE | FALSE | -0.0010774
3.8718 | -216.9636 | -2.7116 | 0.23536 | FALSE | FALSE | FALSE | -0.0010848
3.8779 | -218.4465 | -2.7302 | 0.23859 | FALSE | FALSE | FALSE | -0.0010922
3.8841 | -219.9212 | -2.7486 | 0.24182 | FALSE | FALSE | FALSE | -0.0010996
3.8902 | -221.3875 | -2.7669 | 0.24506 | FALSE | FALSE | FALSE | -0.0011069
3.8963 | -222.8456 | -2.7851 | 0.2483 | FALSE | FALSE | FALSE | -0.0011142
3.9025 | -224.2952 | -2.8033 | 0.25154 | FALSE | FALSE | FALSE | -0.0011215
3.9086 | -225.7364 | -2.8213 | 0.25478 | FALSE | FALSE | FALSE | -0.0011287
3.9148 | -227.1691 | -2.8392 | 0.25803 | FALSE | FALSE | FALSE | -0.0011358
3.9209 | -228.5933 | -2.857 | 0.26127 | FALSE | FALSE | FALSE | -0.001143
3.927 | -230.0088 | -2.8747 | 661.4654 | FALSE | TRUE | TRUE | -2.8758
3.9332 | -231.4157 | -2.8923 | 669.582 | FALSE | TRUE | TRUE | -2.8934
3.9393 | -232.8139 | -2.9097 | 677.6974 | FALSE | TRUE | TRUE | -2.9109
3.9454 | -234.2033 | -2.9271 | 685.8104 | FALSE | TRUE | TRUE | -2.9283
3.9516 | -235.5839 | -2.9444 | 693.9197 | FALSE | TRUE | TRUE | -2.9455
3.9577 | -236.9556 | -2.9615 | 702.0241 | FALSE | TRUE | TRUE | -2.9627
3.9638 | -238.3184 | -2.9785 | 710.1224 | FALSE | TRUE | TRUE | -2.9797
3.97 | -239.6722 | -2.9955 | 718.2133 | FALSE | TRUE | TRUE | -2.9966
3.9761 | -241.017 | -3.0123 | 726.2957 | FALSE | TRUE | TRUE | -3.0135
3.9823 | -242.3527 | -3.029 | 734.3684 | FALSE | TRUE | TRUE | -3.0302
3.9884 | -243.6793 | -3.0455 | 742.43 | FALSE | TRUE | TRUE | -3.0467
3.9945 | -244.9968 | -3.062 | 750.4794 | FALSE | TRUE | TRUE | -3.0632
4.0007 | -246.305 | -3.0783 | 758.5154 | FALSE | TRUE | TRUE | -3.0796
4.0068 | -247.6039 | -3.0946 | 766.5368 | FALSE | TRUE | TRUE | -3.0958
4.0129 | -248.8935 | -3.1107 | 774.5424 | FALSE | TRUE | TRUE | -3.1119
4.0191 | -250.1737 | -3.1267 | 782.5309 | FALSE | TRUE | TRUE | -3.128
4.0252 | -251.4445 | -3.1426 | 790.5012 | FALSE | TRUE | TRUE | -3.1438
4.0313 | -252.7059 | -3.1583 | 798.4521 | FALSE | TRUE | TRUE | -3.1596
4.0375 | -253.9577 | -3.174 | 806.3823 | FALSE | TRUE | TRUE | -3.1753
4.0436 | -255.2 | -3.1895 | 814.2907 | FALSE | TRUE | TRUE | -3.1908
4.0497 | -256.4327 | -3.2049 | 822.176 | FALSE | TRUE | TRUE | -3.2062
4.0559 | -257.6557 | -3.2202 | 830.0372 | FALSE | TRUE | TRUE | -3.2215
4.062 | -258.869 | -3.2354 | 837.8729 | FALSE | TRUE | TRUE | -3.2367
4.0682 | -260.0725 | -3.2504 | 845.6821 | FALSE | TRUE | TRUE | -3.2517
4.0743 | -261.2663 | -3.2653 | 853.4635 | FALSE | TRUE | TRUE | -3.2666
4.0804 | -262.4502 | -3.2801 | 861.216 | FALSE | TRUE | TRUE | -3.2814
4.0866 | -263.6243 | -3.2948 | 868.9385 | FALSE | TRUE | TRUE | -3.2961
4.0927 | -264.7884 | -3.3094 | 876.6296 | FALSE | TRUE | TRUE | -3.3107
4.0988 | -265.9426 | -3.3238 | 884.2884 | FALSE | TRUE | TRUE | -3.3251
4.105 | -267.0867 | -3.3381 | 891.9136 | FALSE | TRUE | TRUE | -3.3394
4.1111 | -268.2208 | -3.3523 | 899.504 | FALSE | TRUE | TRUE | -3.3536
4.1172 | -269.3448 | -3.3663 | 907.0587 | FALSE | TRUE | TRUE | -3.3676
4.1234 | -270.4587 | -3.3802 | 914.5763 | FALSE | TRUE | TRUE | -3.3816
4.1295 | -271.5623 | -3.394 | 922.0558 | FALSE | TRUE | TRUE | -3.3954
4.1357 | -272.6558 | -3.4077 | 929.496 | FALSE | TRUE | TRUE | -3.409
4.1418 | -273.739 | -3.4212 | 936.8959 | FALSE | TRUE | TRUE | -3.4226
4.1479 | -274.8118 | -3.4346 | 944.2543 | FALSE | TRUE | TRUE | -3.436
4.1541 | -275.8743 | -3.4479 | 951.5701 | FALSE | TRUE | TRUE | -3.4493
4.1602 | -276.9265 | -3.4611 | 958.8422 | FALSE | TRUE | TRUE | -3.4624
4.1663 | -277.9682 | -3.4741 | 966.0695 | FALSE | TRUE | TRUE | -3.4755
4.1725 | -278.9994 | -3.487 | 973.2509 | FALSE | TRUE | TRUE | -3.4884
4.1786 | -280.0202 | -3.4997 | 980.3853 | FALSE | TRUE | TRUE | -3.5011
4.1847 | -281.0304 | -3.5123 | 987.4718 | FALSE | TRUE | TRUE | -3.5138
4.1909 | -282.03 | -3.5248 | 994.5091 | FALSE | TRUE | TRUE | -3.5263
4.197 | -283.019 | -3.5372 | 1001.4962 | FALSE | TRUE | TRUE | -3.5386
4.2031 | -283.9973 | -3.5494 | 1008.4322 | FALSE | TRUE | TRUE | -3.5509
4.2093 | -284.965 | -3.5615 | 1015.3158 | FALSE | TRUE | TRUE | -3.5629
4.2154 | -285.9219 | -3.5735 | 1022.1462 | FALSE | TRUE | TRUE | -3.5749
4.2216 | -286.8681 | -3.5853 | 1028.9223 | FALSE | TRUE | TRUE | -3.5867
4.2277 | -287.8034 | -3.597 | 1035.643 | FALSE | TRUE | TRUE | -3.5984
4.2338 | -288.728 | -3.6086 | 1042.3073 | FALSE | TRUE | TRUE | -3.61
4.24 | -289.6416 | -3.62 | 1048.9143 | FALSE | TRUE | TRUE | -3.6214
4.2461 | -290.5443 | -3.6313 | 1055.4629 | FALSE | TRUE | TRUE | -3.6327
4.2522 | -291.4362 | -3.6424 | 1061.9522 | FALSE | TRUE | TRUE | -3.6439
4.2584 | -292.317 | -3.6534 | 1068.3812 | FALSE | TRUE | TRUE | -3.6549
4.2645 | -293.1868 | -3.6643 | 1074.7489 | FALSE | TRUE | TRUE | -3.6657
4.2706 | -294.0456 | -3.675 | 1081.0543 | FALSE | TRUE | TRUE | -3.6765
4.2768 | -294.8933 | -3.6856 | 1087.2965 | FALSE | TRUE | TRUE | -3.6871
4.2829 | -295.7299 | -3.6961 | 1093.4746 | FALSE | TRUE | TRUE | -3.6975
4.2891 | -296.5554 | -3.7064 | 1099.5876 | FALSE | TRUE | TRUE | -3.7079
4.2952 | -297.3697 | -3.7166 | 1105.6347 | FALSE | TRUE | TRUE | -3.718
4.3013 | -298.1729 | -3.7266 | 1111.6148 | FALSE | TRUE | TRUE | -3.7281
4.3075 | -298.9647 | -3.7365 | 1117.5272 | FALSE | TRUE | TRUE | -3.738
4.3136 | -299.7454 | -3.7463 | 1123.3708 | FALSE | TRUE | TRUE | -3.7478
4.3197 | -300.5147 | -3.7559 | 1129.1449 | FALSE | TRUE | TRUE | -3.7574
4.3259 | -301.2728 | -3.7653 | 1134.8485 | FALSE | TRUE | TRUE | -3.7668
4.332 | -302.0195 | -3.7747 | 1140.4809 | FALSE | TRUE | TRUE | -3.7762
4.3381 | -302.7548 | -3.7839 | 1146.041 | FALSE | TRUE | TRUE | -3.7854
4.3443 | -303.4787 | -3.7929 | 1151.5283 | FALSE | TRUE | TRUE | -3.7944
4.3504 | -304.1912 | -3.8018 | 1156.9416 | FALSE | TRUE | TRUE | -3.8033
4.3565 | -304.8923 | -3.8106 | 1162.2804 | FALSE | TRUE | TRUE | -3.8121
4.3627 | -305.5818 | -3.8192 | 1167.5438 | FALSE | TRUE | TRUE | -3.8207
4.3688 | -306.2599 | -3.8277 | 1172.7309 | FALSE | TRUE | TRUE | -3.8292
4.375 | -306.9264 | -3.836 | 1177.841 | FALSE | TRUE | TRUE | -3.8375
4.3811 | -307.5814 | -3.8442 | 1182.8733 | FALSE | TRUE | TRUE | -3.8457
4.3872 | -308.2248 | -3.8522 | 1187.8271 | FALSE | TRUE | TRUE | -3.8538
4.3934 | -308.8566 | -3.8601 | 1192.7017 | FALSE | TRUE | TRUE | -3.8617
4.3995 | -309.4767 | -3.8679 | 1197.4962 | FALSE | TRUE | TRUE | -3.8694
4.4056 | -310.0852 | -3.8755 | 1202.21 | FALSE | TRUE | TRUE | -3.877
4.4118 | -310.6821 | -3.8829 | 1206.8423 | FALSE | TRUE | TRUE | -3.8845
4.4179 | -311.2672 | -3.8903 | 1211.3925 | FALSE | TRUE | TRUE | -3.8918
4.424 | -311.8406 | -3.8974 | 1215.8599 | FALSE | TRUE | TRUE | -3.899
4.4302 | -312.4023 | -3.9044 | 1220.2438 | FALSE | TRUE | TRUE | -3.906
4.4363 | -312.9522 | -3.9113 | 1224.5435 | FALSE | TRUE | TRUE | -3.9129
4.4425 | -313.4904 | -3.918 | 1228.7584 | FALSE | TRUE | TRUE | -3.9196
4.4486 | -314.0167 | -3.9246 | 1232.8879 | FALSE | TRUE | TRUE | -3.9262
4.4547 | -314.5312 | -3.931 | 1236.9313 | FALSE | TRUE | TRUE | -3.9326
4.4609 | -315.0339 | -3.9373 | 1240.888 | FALSE | TRUE | TRUE | -3.9389
4.467 | -315.5247 | -3.9435 | 1244.7575 | FALSE | TRUE | TRUE | -3.945
4.4731 | -316.0036 | -3.9494 | 1248.5391 | FALSE | TRUE | TRUE | -3.951
4.4793 | -316.4706 | -3.9553 | 1252.2323 | FALSE | TRUE | TRUE | -3.9569
4.4854 | -316.9257 | -3.961 | 1255.8365 | FALSE | TRUE | TRUE | -3.9626
4.4915 | -317.3689 | -3.9665 | 1259.3512 | FALSE | TRUE | TRUE | -3.9681
4.4977 | -317.8001 | -3.9719 | 1262.7758 | FALSE | TRUE | TRUE | -3.9735
4.5038 | -318.2194 | -3.9771 | 1266.1099 | FALSE | TRUE | TRUE | -3.9787
4.5099 | -318.6267 | -3.9822 | 1269.353 | FALSE | TRUE | TRUE | -3.9838
4.5161 | -319.022 | -3.9872 | 1272.5044 | FALSE | TRUE | TRUE | -3.9888
4.5222 | -319.4052 | -3.992 | 1275.5638 | FALSE | TRUE | TRUE | -3.9936
4.5284 | -319.7765 | -3.9966 | 1278.5308 | FALSE | TRUE | TRUE | -3.9982
4.5345 | -320.1357 | -4.0011 | 1281.4048 | FALSE | TRUE | TRUE | -4.0027
4.5406 | -320.4829 | -4.0054 | 1284.1854 | FALSE | TRUE | TRUE | -4.007
4.5468 | -320.8179 | -4.0096 | 1286.8723 | FALSE | TRUE | TRUE | -4.0112
4.5529 | -321.141 | -4.0137 | 1289.4649 | FALSE | TRUE | TRUE | -4.0153
4.559 | -321.4519 | -4.0175 | 1291.963 | FALSE | TRUE | TRUE | -4.0191
4.5652 | -321.7507 | -4.0213 | 1294.3661 | FALSE | TRUE | TRUE | -4.0229
4.5713 | -322.0374 | -4.0249 | 1296.6739 | FALSE | TRUE | TRUE | -4.0265
4.5774 | -322.312 | -4.0283 | 1298.886 | FALSE | TRUE | TRUE | -4.0299
4.5836 | -322.5744 | -4.0316 | 1301.0021 | FALSE | TRUE | TRUE | -4.0332
4.5897 | -322.8247 | -4.0347 | 1303.0219 | FALSE | TRUE | TRUE | -4.0363
4.5959 | -323.0629 | -4.0377 | 1304.9451 | FALSE | TRUE | TRUE | -4.0393
4.602 | -323.2889 | -4.0405 | 1306.7713 | FALSE | TRUE | TRUE | -4.0421
4.6081 | -323.5027 | -4.0432 | 1308.5004 | FALSE | TRUE | TRUE | -4.0448
4.6143 | -323.7043 | -4.0457 | 1310.132 | FALSE | TRUE | TRUE | -4.0473
4.6204 | -323.8937 | -4.0481 | 1311.6659 | FALSE | TRUE | TRUE | -4.0497
4.6265 | -324.071 | -4.0503 | 1313.1019 | FALSE | TRUE | TRUE | -4.0519
4.6327 | -324.236 | -4.0523 | 1314.4398 | FALSE | TRUE | TRUE | -4.054
4.6388 | -324.3889 | -4.0542 | 1315.6793 | FALSE | TRUE | TRUE | -4.0559
4.6449 | -324.5295 | -4.056 | 1316.8202 | FALSE | TRUE | TRUE | -4.0576
4.6511 | -324.6579 | -4.0576 | 1317.8625 | FALSE | TRUE | TRUE | -4.0592
4.6572 | -324.7741 | -4.0591 | 1318.8059 | FALSE | TRUE | TRUE | -4.0607
4.6633 | -324.878 | -4.0604 | 1319.6503 | FALSE | TRUE | TRUE | -4.062
4.6695 | -324.9698 | -4.0615 | 1320.3956 | FALSE | TRUE | TRUE | -4.0631
4.6756 | -325.0493 | -4.0625 | 1321.0416 | FALSE | TRUE | TRUE | -4.0641
4.6818 | -325.1165 | -4.0633 | 1321.5883 | FALSE | TRUE | TRUE | -4.065
4.6879 | -325.1715 | -4.064 | 1322.0355 | FALSE | TRUE | TRUE | -4.0657
4.694 | -325.2143 | -4.0646 | 1322.3833 | FALSE | TRUE | TRUE | -4.0662
4.7002 | -325.2448 | -4.0649 | 1322.6316 | FALSE | TRUE | TRUE | -4.0666
4.7063 | -325.2631 | -4.0652 | 1322.7802 | FALSE | TRUE | TRUE | -4.0668
4.7124 | -325.2691 | -4.0652 | 1322.8293 | FALSE | TRUE | TRUE | -4.0669
4.7186 | -325.2629 | -4.0652 | 1322.7787 | FALSE | TRUE | TRUE | -4.0668
4.7247 | -325.2444 | -4.0649 | 1322.6286 | FALSE | TRUE | TRUE | -4.0666
4.7308 | -325.2137 | -4.0646 | 1322.3788 | FALSE | TRUE | TRUE | -4.0662
4.737 | -325.1708 | -4.064 | 1322.0296 | FALSE | TRUE | TRUE | -4.0656
4.7431 | -325.1156 | -4.0633 | 1321.5808 | FALSE | TRUE | TRUE | -4.065
4.7493 | -325.0482 | -4.0625 | 1321.0326 | FALSE | TRUE | TRUE | -4.0641
4.7554 | -324.9685 | -4.0615 | 1320.3851 | FALSE | TRUE | TRUE | -4.0631
4.7615 | -324.8766 | -4.0603 | 1319.6384 | FALSE | TRUE | TRUE | -4.062
4.7677 | -324.7724 | -4.059 | 1318.7925 | FALSE | TRUE | TRUE | -4.0607
4.7738 | -324.6561 | -4.0576 | 1317.8476 | FALSE | TRUE | TRUE | -4.0592
4.7799 | -324.5275 | -4.056 | 1316.8038 | FALSE | TRUE | TRUE | -4.0576
4.7861 | -324.3867 | -4.0542 | 1315.6614 | FALSE | TRUE | TRUE | -4.0558
4.7922 | -324.2336 | -4.0523 | 1314.4204 | FALSE | TRUE | TRUE | -4.0539
4.7983 | -324.0684 | -4.0502 | 1313.0811 | FALSE | TRUE | TRUE | -4.0519
4.8045 | -323.891 | -4.048 | 1311.6436 | FALSE | TRUE | TRUE | -4.0496
4.8106 | -323.7014 | -4.0457 | 1310.1083 | FALSE | TRUE | TRUE | -4.0473
4.8167 | -323.4995 | -4.0431 | 1308.4752 | FALSE | TRUE | TRUE | -4.0448
4.8229 | -323.2856 | -4.0405 | 1306.7447 | FALSE | TRUE | TRUE | -4.0421
4.829 | -323.0594 | -4.0376 | 1304.917 | FALSE | TRUE | TRUE | -4.0392
4.8352 | -322.8211 | -4.0347 | 1302.9923 | FALSE | TRUE | TRUE | -4.0363
4.8413 | -322.5706 | -4.0315 | 1300.9711 | FALSE | TRUE | TRUE | -4.0331
4.8474 | -322.308 | -4.0282 | 1298.8535 | FALSE | TRUE | TRUE | -4.0299
4.8536 | -322.0332 | -4.0248 | 1296.64 | FALSE | TRUE | TRUE | -4.0264
4.8597 | -321.7463 | -4.0212 | 1294.3308 | FALSE | TRUE | TRUE | -4.0228
4.8658 | -321.4473 | -4.0175 | 1291.9262 | FALSE | TRUE | TRUE | -4.0191
4.872 | -321.1362 | -4.0136 | 1289.4267 | FALSE | TRUE | TRUE | -4.0152
4.8781 | -320.813 | -4.0096 | 1286.8327 | FALSE | TRUE | TRUE | -4.0112
4.8842 | -320.4777 | -4.0054 | 1284.1444 | FALSE | TRUE | TRUE | -4.007
4.8904 | -320.1304 | -4.001 | 1281.3624 | FALSE | TRUE | TRUE | -4.0026
4.8965 | -319.771 | -3.9965 | 1278.487 | FALSE | TRUE | TRUE | -3.9981
4.9027 | -319.3996 | -3.9919 | 1275.5186 | FALSE | TRUE | TRUE | -3.9935
4.9088 | -319.0161 | -3.9871 | 1272.4578 | FALSE | TRUE | TRUE | -3.9887
4.9149 | -318.6207 | -3.9822 | 1269.305 | FALSE | TRUE | TRUE | -3.9837
4.9211 | -318.2132 | -3.9771 | 1266.0606 | FALSE | TRUE | TRUE | -3.9787
4.9272 | -317.7937 | -3.9718 | 1262.7251 | FALSE | TRUE | TRUE | -3.9734
4.9333 | -317.3623 | -3.9664 | 1259.2991 | FALSE | TRUE | TRUE | -3.968
4.9395 | -316.919 | -3.9609 | 1255.7831 | FALSE | TRUE | TRUE | -3.9625
4.9456 | -316.4637 | -3.9552 | 1252.1775 | FALSE | TRUE | TRUE | -3.9568
4.9517 | -315.9965 | -3.9494 | 1248.483 | FALSE | TRUE | TRUE | -3.9509
4.9579 | -315.5174 | -3.9434 | 1244.7001 | FALSE | TRUE | TRUE | -3.9449
4.964 | -315.0264 | -3.9372 | 1240.8293 | FALSE | TRUE | TRUE | -3.9388
4.9701 | -314.5236 | -3.931 | 1236.8713 | FALSE | TRUE | TRUE | -3.9325
4.9763 | -314.0089 | -3.9245 | 1232.8266 | FALSE | TRUE | TRUE | -3.9261
4.9824 | -313.4824 | -3.9179 | 1228.6958 | FALSE | TRUE | TRUE | -3.9195
4.9886 | -312.9441 | -3.9112 | 1224.4796 | FALSE | TRUE | TRUE | -3.9128
4.9947 | -312.394 | -3.9043 | 1220.1786 | FALSE | TRUE | TRUE | -3.9059
5.0008 | -311.8321 | -3.8973 | 1215.7935 | FALSE | TRUE | TRUE | -3.8989
5.007 | -311.2585 | -3.8901 | 1211.3249 | FALSE | TRUE | TRUE | -3.8917
5.0131 | -310.6732 | -3.8828 | 1206.7734 | FALSE | TRUE | TRUE | -3.8844
5.0192 | -310.0762 | -3.8754 | 1202.1399 | FALSE | TRUE | TRUE | -3.8769
5.0254 | -309.4675 | -3.8678 | 1197.4249 | FALSE | TRUE | TRUE | -3.8693
5.0315 | -308.8472 | -3.86 | 1192.6291 | FALSE | TRUE | TRUE | -3.8616
5.0376 | -308.2152 | -3.8521 | 1187.7534 | FALSE | TRUE | TRUE | -3.8536
5.0438 | -307.5716 | -3.8441 | 1182.7984 | FALSE | TRUE | TRUE | -3.8456
5.0499 | -306.9165 | -3.8359 | 1177.7649 | FALSE | TRUE | TRUE | -3.8374
5.0561 | -306.2498 | -3.8275 | 1172.6536 | FALSE | TRUE | TRUE | -3.8291
5.0622 | -305.5716 | -3.8191 | 1167.4654 | FALSE | TRUE | TRUE | -3.8206
5.0683 | -304.8818 | -3.8104 | 1162.2009 | FALSE | TRUE | TRUE | -3.812
5.0745 | -304.1806 | -3.8017 | 1156.861 | FALSE | TRUE | TRUE | -3.8032
5.0806 | -303.4679 | -3.7928 | 1151.4465 | FALSE | TRUE | TRUE | -3.7943
5.0867 | -302.7438 | -3.7837 | 1145.9582 | FALSE | TRUE | TRUE | -3.7852
5.0929 | -302.0083 | -3.7745 | 1140.3969 | FALSE | TRUE | TRUE | -3.776
5.099 | -301.2615 | -3.7652 | 1134.7635 | FALSE | TRUE | TRUE | -3.7667
5.1051 | -300.5033 | -3.7557 | 1129.0588 | FALSE | TRUE | TRUE | -3.7572
5.1113 | -299.7338 | -3.7461 | 1123.2837 | FALSE | TRUE | TRUE | -3.7476
5.1174 | -298.9529 | -3.7363 | 1117.439 | FALSE | TRUE | TRUE | -3.7378
5.1235 | -298.1609 | -3.7264 | 1111.5256 | FALSE | TRUE | TRUE | -3.7279
5.1297 | -297.3576 | -3.7164 | 1105.5445 | FALSE | TRUE | TRUE | -3.7179
5.1358 | -296.5431 | -3.7062 | 1099.4964 | FALSE | TRUE | TRUE | -3.7077
5.142 | -295.7175 | -3.6959 | 1093.3824 | FALSE | TRUE | TRUE | -3.6974
5.1481 | -294.8807 | -3.6855 | 1087.2034 | FALSE | TRUE | TRUE | -3.6869
5.1542 | -294.0328 | -3.6749 | 1080.9602 | FALSE | TRUE | TRUE | -3.6763
5.1604 | -293.1738 | -3.6641 | 1074.6538 | FALSE | TRUE | TRUE | -3.6656
5.1665 | -292.3039 | -3.6532 | 1068.2852 | FALSE | TRUE | TRUE | -3.6547
5.1726 | -291.4229 | -3.6422 | 1061.8553 | FALSE | TRUE | TRUE | -3.6437
5.1788 | -290.5309 | -3.6311 | 1055.3651 | FALSE | TRUE | TRUE | -3.6325
5.1849 | -289.628 | -3.6198 | 1048.8156 | FALSE | TRUE | TRUE | -3.6213
5.191 | -288.7142 | -3.6084 | 1042.2078 | FALSE | TRUE | TRUE | -3.6098
5.1972 | -287.7895 | -3.5968 | 1035.5426 | FALSE | TRUE | TRUE | -3.5983
5.2033 | -286.854 | -3.5851 | 1028.821 | FALSE | TRUE | TRUE | -3.5866
5.2094 | -285.9076 | -3.5733 | 1022.0442 | FALSE | TRUE | TRUE | -3.5747
5.2156 | -284.9506 | -3.5613 | 1015.213 | FALSE | TRUE | TRUE | -3.5628
5.2217 | -283.9827 | -3.5492 | 1008.3285 | FALSE | TRUE | TRUE | -3.5507
5.2279 | -283.0042 | -3.537 | 1001.3918 | FALSE | TRUE | TRUE | -3.5384
5.234 | -282.0151 | -3.5247 | 994.4039 | FALSE | TRUE | TRUE | -3.5261
5.2401 | -281.0153 | -3.5122 | 987.3658 | FALSE | TRUE | TRUE | -3.5136
5.2463 | -280.005 | -3.4995 | 980.2787 | FALSE | TRUE | TRUE | -3.5009
5.2524 | -278.9841 | -3.4868 | 973.1435 | FALSE | TRUE | TRUE | -3.4882
5.2585 | -277.9526 | -3.4739 | 965.9614 | FALSE | TRUE | TRUE | -3.4753
5.2647 | -276.9108 | -3.4609 | 958.7334 | FALSE | TRUE | TRUE | -3.4622
5.2708 | -275.8585 | -3.4477 | 951.4607 | FALSE | TRUE | TRUE | -3.4491
5.2769 | -274.7958 | -3.4344 | 944.1442 | FALSE | TRUE | TRUE | -3.4358
5.2831 | -273.7228 | -3.421 | 936.7852 | FALSE | TRUE | TRUE | -3.4224
5.2892 | -272.6394 | -3.4075 | 929.3847 | FALSE | TRUE | TRUE | -3.4088
5.2954 | -271.5459 | -3.3938 | 921.9439 | FALSE | TRUE | TRUE | -3.3952
5.3015 | -270.442 | -3.38 | 914.4638 | FALSE | TRUE | TRUE | -3.3814
5.3076 | -269.328 | -3.3661 | 906.9456 | FALSE | TRUE | TRUE | -3.3674
5.3138 | -268.2039 | -3.352 | 899.3904 | FALSE | TRUE | TRUE | -3.3534
5.3199 | -267.0696 | -3.3379 | 891.7994 | FALSE | TRUE | TRUE | -3.3392
5.326 | -265.9254 | -3.3236 | 884.1737 | FALSE | TRUE | TRUE | -3.3249
5.3322 | -264.771 | -3.3091 | 876.5145 | FALSE | TRUE | TRUE | -3.3105
5.3383 | -263.6068 | -3.2946 | 868.8229 | FALSE | TRUE | TRUE | -3.2959
5.3444 | -262.4326 | -3.2799 | 861.1 | FALSE | TRUE | TRUE | -3.2812
5.3506 | -261.2485 | -3.2651 | 853.347 | FALSE | TRUE | TRUE | -3.2664
5.3567 | -260.0546 | -3.2502 | 845.5652 | FALSE | TRUE | TRUE | -3.2515
5.3628 | -258.8509 | -3.2351 | 837.7556 | FALSE | TRUE | TRUE | -3.2364
5.369 | -257.6374 | -3.22 | 829.9195 | FALSE | TRUE | TRUE | -3.2213
5.3751 | -256.4142 | -3.2047 | 822.0579 | FALSE | TRUE | TRUE | -3.206
5.3813 | -255.1814 | -3.1893 | 814.1722 | FALSE | TRUE | TRUE | -3.1906
5.3874 | -253.939 | -3.1738 | 806.2635 | FALSE | TRUE | TRUE | -3.175
5.3935 | -252.687 | -3.1581 | 798.333 | FALSE | TRUE | TRUE | -3.1594
5.3997 | -251.4255 | -3.1423 | 790.3818 | FALSE | TRUE | TRUE | -3.1436
5.4058 | -250.1546 | -3.1265 | 782.4112 | FALSE | TRUE | TRUE | -3.1277
5.4119 | -248.8742 | -3.1105 | 774.4225 | FALSE | TRUE | TRUE | -3.1117
5.4181 | -247.5845 | -3.0943 | 766.4166 | FALSE | TRUE | TRUE | -3.0956
5.4242 | -246.2854 | -3.0781 | 758.395 | FALSE | TRUE | TRUE | -3.0793
5.4303 | -244.9771 | -3.0618 | 750.3588 | FALSE | TRUE | TRUE | -3.063
5.4365 | -243.6595 | -3.0453 | 742.3092 | FALSE | TRUE | TRUE | -3.0465
5.4426 | -242.3328 | -3.0287 | 734.2473 | FALSE | TRUE | TRUE | -3.0299
5.4488 | -240.9969 | -3.012 | 726.1746 | FALSE | TRUE | TRUE | -3.0132
5.4549 | -239.652 | -2.9952 | 718.092 | FALSE | TRUE | TRUE | -2.9964
5.461 | -238.298 | -2.9783 | 710.001 | FALSE | TRUE | TRUE | -2.9795
5.4672 | -236.9351 | -2.9612 | 701.9026 | FALSE | TRUE | TRUE | -2.9624
5.4733 | -235.5632 | -2.9441 | 693.7981 | FALSE | TRUE | TRUE | -2.9453
5.4794 | -234.1825 | -2.9268 | 685.6887 | FALSE | TRUE | TRUE | -2.928
5.4856 | -232.793 | -2.9095 | 677.5757 | FALSE | TRUE | TRUE | -2.9106
5.4917 | -231.3947 | -2.892 | 669.4603 | FALSE | TRUE | TRUE | -2.8932
5.4978 | -229.9877 | -2.8744 | 0.26447 | FALSE | FALSE | FALSE | -0.0011499
5.504 | -228.572 | -2.8567 | 0.26122 | FALSE | FALSE | FALSE | -0.0011428
5.5101 | -227.1477 | -2.8389 | 0.25798 | FALSE | FALSE | FALSE | -0.0011357
5.5162 | -225.7149 | -2.821 | 0.25473 | FALSE | FALSE | FALSE | -0.0011286
5.5224 | -224.2735 | -2.803 | 0.25149 | FALSE | FALSE | FALSE | -0.0011214
5.5285 | -222.8238 | -2.7849 | 0.24825 | FALSE | FALSE | FALSE | -0.0011141
5.5347 | -221.3656 | -2.7667 | 0.24501 | FALSE | FALSE | FALSE | -0.0011068
5.5408 | -219.8991 | -2.7483 | 0.24178 | FALSE | FALSE | FALSE | -0.0010995
5.5469 | -218.4243 | -2.7299 | 0.23854 | FALSE | FALSE | FALSE | -0.0010921
5.5531 | -216.9413 | -2.7114 | 0.23532 | FALSE | FALSE | FALSE | -0.0010847
5.5592 | -215.4502 | -2.6927 | 0.23209 | FALSE | FALSE | FALSE | -0.0010772
5.5653 | -213.9509 | -2.674 | 0.22887 | FALSE | FALSE | FALSE | -0.0010697
5.5715 | -212.4436 | -2.6551 | 0.22566 | FALSE | FALSE | FALSE | -0.0010622
5.5776 | -210.9282 | -2.6362 | 0.22245 | FALSE | FALSE | FALSE | -0.0010546
5.5837 | -209.4049 | -2.6172 | 0.21925 | FALSE | FALSE | FALSE | -0.001047
5.5899 | -207.8738 | -2.598 | 0.21606 | FALSE | FALSE | FALSE | -0.0010394
5.596 | -206.3348 | -2.5788 | 0.21287 | FALSE | FALSE | FALSE | -0.0010317
5.6022 | -204.7881 | -2.5595 | 0.20969 | FALSE | FALSE | FALSE | -0.0010239
5.6083 | -203.2336 | -2.54 | 0.20652 | FALSE | FALSE | FALSE | -0.0010162
5.6144 | -201.6715 | -2.5205 | 0.20335 | FALSE | FALSE | FALSE | -0.0010083
5.6206 | -200.1018 | -2.5009 | 0.2002 | FALSE | FALSE | FALSE | -0.0010005
5.6267 | -198.5245 | -2.4812 | 0.19706 | FALSE | FALSE | FALSE | -0.00099261
5.6328 | -196.9398 | -2.4614 | 0.19392 | FALSE | FALSE | FALSE | -0.00098469
5.639 | -195.3477 | -2.4415 | 0.1908 | FALSE | FALSE | FALSE | -0.00097673
5.6451 | -193.7482 | -2.4215 | 0.18769 | FALSE | FALSE | FALSE | -0.00096873
5.6512 | -192.1414 | -2.4014 | 0.18459 | FALSE | FALSE | FALSE | -0.0009607
5.6574 | -190.5274 | -2.3812 | 0.1815 | FALSE | FALSE | FALSE | -0.00095263
5.6635 | -188.9062 | -2.361 | 0.17843 | FALSE | FALSE | FALSE | -0.00094452
5.6696 | -187.2779 | -2.3406 | 0.17536 | FALSE | FALSE | FALSE | -0.00093638
5.6758 | -185.6425 | -2.3202 | 0.17231 | FALSE | FALSE | FALSE | -0.0009282
5.6819 | -184.0002 | -2.2997 | 0.16928 | FALSE | FALSE | FALSE | -0.00091999
5.6881 | -182.3509 | -2.279 | 0.16626 | FALSE | FALSE | FALSE | -0.00091175
5.6942 | -180.6948 | -2.2583 | 0.16325 | FALSE | FALSE | FALSE | -0.00090347
5.7003 | -179.0319 | -2.2376 | 0.16026 | FALSE | FALSE | FALSE | -0.00089515
5.7065 | -177.3622 | -2.2167 | 0.15729 | FALSE | FALSE | FALSE | -0.0008868
5.7126 | -175.6858 | -2.1957 | 0.15433 | FALSE | FALSE | FALSE | -0.00087842
5.7187 | -174.0029 | -2.1747 | 0.15138 | FALSE | FALSE | FALSE | -0.00087001
5.7249 | -172.3133 | -2.1536 | 0.14846 | FALSE | FALSE | FALSE | -0.00086156
5.731 | -170.6173 | -2.1324 | 0.14555 | FALSE | FALSE | FALSE | -0.00085308
5.7371 | -168.9149 | -2.1111 | 0.14266 | FALSE | FALSE | FALSE | -0.00084457
5.7433 | -167.2061 | -2.0898 | 0.13979 | FALSE | FALSE | FALSE | -0.00083602
5.7494 | -165.491 | -2.0683 | 0.13694 | FALSE | FALSE | FALSE | -0.00082745
5.7556 | -163.7697 | -2.0468 | 0.1341 | FALSE | FALSE | FALSE | -0.00081884
5.7617 | -162.0422 | -2.0252 | 0.13129 | FALSE | FALSE | FALSE | -0.0008102
5.7678 | -160.3086 | -2.0036 | 0.12849 | FALSE | FALSE | FALSE | -0.00080154
5.774 | -158.569 | -1.9818 | 0.12572 | FALSE | FALSE | FALSE | -0.00079284
5.7801 | -156.8234 | -1.96 | 0.12297 | FALSE | FALSE | FALSE | -0.00078411
5.7862 | -155.0719 | -1.9381 | 0.12024 | FALSE | FALSE | FALSE | -0.00077535
5.7924 | -153.3146 | -1.9161 | 0.11753 | FALSE | FALSE | FALSE | -0.00076657
5.7985 | -151.5515 | -1.8941 | 0.11484 | FALSE | FALSE | FALSE | -0.00075775
5.8046 | -149.7827 | -1.872 | 0.11217 | FALSE | FALSE | FALSE | -0.00074891
5.8108 | -148.0082 | -1.8498 | 0.10953 | FALSE | FALSE | FALSE | -0.00074003
5.8169 | -146.2282 | -1.8276 | 0.10691 | FALSE | FALSE | FALSE | -0.00073113
5.823 | -144.4426 | -1.8053 | 0.10432 | FALSE | FALSE | FALSE | -0.00072221
5.8292 | -142.6517 | -1.7829 | 0.10175 | FALSE | FALSE | FALSE | -0.00071325
5.8353 | -140.8553 | -1.7604 | 0.0992 | FALSE | FALSE | FALSE | -0.00070427
5.8415 | -139.0537 | -1.7379 | 0.096679 | FALSE | FALSE | FALSE | -0.00069526
5.8476 | -137.2468 | -1.7153 | 0.094183 | FALSE | FALSE | FALSE | -0.00068623
5.8537 | -135.4348 | -1.6927 | 0.091712 | FALSE | FALSE | FALSE | -0.00067717
5.8599 | -133.6176 | -1.67 | 0.089267 | FALSE | FALSE | FALSE | -0.00066808
5.866 | -131.7955 | -1.6472 | 0.086849 | FALSE | FALSE | FALSE | -0.00065897
5.8721 | -129.9683 | -1.6244 | 0.084458 | FALSE | FALSE | FALSE | -0.00064984
5.8783 | -128.1363 | -1.6015 | 0.082094 | FALSE | FALSE | FALSE | -0.00064068
5.8844 | -126.2994 | -1.5785 | 0.079757 | FALSE | FALSE | FALSE | -0.00063149
5.8905 | -124.4578 | -1.5555 | 0.077448 | FALSE | FALSE | FALSE | -0.00062228
5.8967 | -122.6115 | -1.5324 | 0.075167 | FALSE | FALSE | FALSE | -0.00061305
5.9028 | -120.7606 | -1.5093 | 0.072915 | FALSE | FALSE | FALSE | -0.0006038
5.909 | -118.9051 | -1.4861 | 0.070691 | FALSE | FALSE | FALSE | -0.00059452
5.9151 | -117.0452 | -1.4628 | 0.068497 | FALSE | FALSE | FALSE | -0.00058522
5.9212 | -115.1809 | -1.4395 | 0.066333 | FALSE | FALSE | FALSE | -0.0005759
5.9274 | -113.3122 | -1.4162 | 0.064198 | FALSE | FALSE | FALSE | -0.00056656
5.9335 | -111.4392 | -1.3928 | 0.062093 | FALSE | FALSE | FALSE | -0.00055719
5.9396 | -109.5621 | -1.3693 | 0.060019 | FALSE | FALSE | FALSE | -0.00054781
5.9458 | -107.6808 | -1.3458 | 0.057975 | FALSE | FALSE | FALSE | -0.0005384
5.9519 | -105.7955 | -1.3222 | 0.055963 | FALSE | FALSE | FALSE | -0.00052897
5.958 | -103.9062 | -1.2986 | 0.053982 | FALSE | FALSE | FALSE | -0.00051953
5.9642 | -102.013 | -1.275 | 0.052033 | FALSE | FALSE | FALSE | -0.00051006
5.9703 | -100.1159 | -1.2513 | 0.050116 | FALSE | FALSE | FALSE | -0.00050057
5.9764 | -98.2151 | -1.2275 | 0.048231 | FALSE | FALSE | FALSE | -0.00049107
5.9826 | -96.3106 | -1.2037 | 0.046378 | FALSE | FALSE | FALSE | -0.00048155
5.9887 | -94.4024 | -1.1799 | 0.044559 | FALSE | FALSE | FALSE | -0.00047201
5.9949 | -92.4907 | -1.156 | 0.042772 | FALSE | FALSE | FALSE | -0.00046245
6.001 | -90.5755 | -1.132 | 0.041019 | FALSE | FALSE | FALSE | -0.00045287
6.0071 | -88.6569 | -1.108 | 0.0393 | FALSE | FALSE | FALSE | -0.00044328
6.0133 | -86.735 | -1.084 | 0.037614 | FALSE | FALSE | FALSE | -0.00043367
6.0194 | -84.8098 | -1.06 | 0.035963 | FALSE | FALSE | FALSE | -0.00042405
6.0255 | -82.8814 | -1.0359 | 0.034346 | FALSE | FALSE | FALSE | -0.0004144
6.0317 | -80.9499 | -1.0117 | 0.032764 | FALSE | FALSE | FALSE | -0.00040475
6.0378 | -79.0153 | -0.98754 | 0.031217 | FALSE | FALSE | FALSE | -0.00039507
6.0439 | -77.0778 | -0.96333 | 0.029705 | FALSE | FALSE | FALSE | -0.00038539
6.0501 | -75.1374 | -0.93908 | 0.028228 | FALSE | FALSE | FALSE | -0.00037568
6.0562 | -73.1941 | -0.91479 | 0.026787 | FALSE | FALSE | FALSE | -0.00036597
6.0624 | -71.2481 | -0.89047 | 0.025381 | FALSE | FALSE | FALSE | -0.00035624
6.0685 | -69.2994 | -0.86611 | 0.024012 | FALSE | FALSE | FALSE | -0.00034649
6.0746 | -67.3481 | -0.84172 | 0.022679 | FALSE | FALSE | FALSE | -0.00033674
6.0808 | -65.3942 | -0.8173 | 0.021382 | FALSE | FALSE | FALSE | -0.00032697
6.0869 | -63.4379 | -0.79285 | 0.020122 | FALSE | FALSE | FALSE | -0.00031719
6.093 | -61.4792 | -0.76837 | 0.018898 | FALSE | FALSE | FALSE | -0.00030739
6.0992 | -59.5182 | -0.74386 | 0.017712 | FALSE | FALSE | FALSE | -0.00029759
6.1053 | -57.5549 | -0.71933 | 0.016563 | FALSE | FALSE | FALSE | -0.00028777
6.1114 | -55.5895 | -0.69476 | 0.015451 | FALSE | FALSE | FALSE | -0.00027794
6.1176 | -53.622 | -0.67017 | 0.014376 | FALSE | FALSE | FALSE | -0.00026811
6.1237 | -51.6524 | -0.64556 | 0.01334 | FALSE | FALSE | FALSE | -0.00025826
6.1298 | -49.681 | -0.62092 | 0.012341 | FALSE | FALSE | FALSE | -0.0002484
6.136 | -47.7076 | -0.59626 | 0.01138 | FALSE | FALSE | FALSE | -0.00023854
6.1421 | -45.7325 | -0.57157 | 0.010457 | FALSE | FALSE | FALSE | -0.00022866
6.1483 | -43.7556 | -0.54686 | 0.0095727 | FALSE | FALSE | FALSE | -0.00021878
6.1544 | -41.7771 | -0.52213 | 0.0087265 | FALSE | FALSE | FALSE | -0.00020888
6.1605 | -39.797 | -0.49739 | 0.0079189 | FALSE | FALSE | FALSE | -0.00019898
6.1667 | -37.8154 | -0.47262 | 0.00715 | FALSE | FALSE | FALSE | -0.00018908
6.1728 | -35.8324 | -0.44784 | 0.0064197 | FALSE | FALSE | FALSE | -0.00017916
6.1789 | -33.848 | -0.42304 | 0.0057284 | FALSE | FALSE | FALSE | -0.00016924
6.1851 | -31.8624 | -0.39822 | 0.005076 | FALSE | FALSE | FALSE | -0.00015931
6.1912 | -29.8756 | -0.37339 | 0.0044627 | FALSE | FALSE | FALSE | -0.00014938
6.1973 | -27.8876 | -0.34854 | 0.0038886 | FALSE | FALSE | FALSE | -0.00013944
6.2035 | -25.8986 | -0.32368 | 0.0033537 | FALSE | FALSE | FALSE | -0.00012949
6.2096 | -23.9086 | -0.29881 | 0.0028581 | FALSE | FALSE | FALSE | -0.00011954
6.2158 | -21.9177 | -0.27393 | 0.0024019 | FALSE | FALSE | FALSE | -0.00010959
6.2219 | -19.926 | -0.24904 | 0.0019852 | FALSE | FALSE | FALSE | -9.9629e-05
6.228 | -17.9336 | -0.22414 | 0.001608 | FALSE | FALSE | FALSE | -8.9667e-05
6.2342 | -15.9404 | -0.19923 | 0.0012705 | FALSE | FALSE | FALSE | -7.9701e-05
6.2403 | -13.9467 | -0.17431 | 0.00097254 | FALSE | FALSE | FALSE | -6.9733e-05
6.2464 | -11.9524 | -0.14938 | 0.0007143 | FALSE | FALSE | FALSE | -5.9762e-05
6.2526 | -9.9577 | -0.12445 | 0.00049578 | FALSE | FALSE | FALSE | -4.9788e-05
6.2587 | -7.9626 | -0.099518 | 0.00031701 | FALSE | FALSE | FALSE | -3.9813e-05
6.2648 | -5.9672 | -0.074579 | 0.00017804 | FALSE | FALSE | FALSE | -2.9836e-05
6.271 | -3.9716 | -0.049638 | 7.8869e-05 | FALSE | FALSE | FALSE | -1.9858e-05
6.2771 | -1.9759 | -0.024695 | 1.952e-05 | FALSE | FALSE | FALSE | -9.8793e-06
6.2832 | 0.019958 | 0.00024944 | 1.9917e-09 | FALSE | FALSE | FALSE | 9.9791e-08
2

## 3-12
Analysis for IEC61000-4-7 & IEC61000-3-12 Harmonics Calibration & Verification protocol | [10 empty] | Harm . No. | Ideal | Min | Max |  |  |  | Rsce choices
Mathieu van den Bergh 2013/2014 | [10 empty] | 1 | 22.2249 | Tolerance |  |  |  |  | 33
[11 empty] | 3 | 2.2322 | 2.1206 | 2.3382 |  |  |  | 66
Change the Rsce, Load resistance(s) and Start-Stop Phase in highlighted fields as desired, then wait for the re-computation | [10 empty] | 5 | 0.74414 | 0.67198 | 0.81631 |  |  |  | 120
[11 empty] | 7 | 0.74407 | 0.67191 | 0.81624 |  |  |  | 250
Select Rsce | 33 |  |  | Calculated parameters | [6 empty] | 9 | 0.44654 | 0.37438 | 0.51871 |  |  |  | >350
Linear load value: | 13.89 | Ohm |  | Linear Load resistance: | 13.89 | Ohm |  |  |  |  | 11 | 0.44648 | 0.37431 | 0.51864
Contr. Load value: | 32.65 | Ohm |  | Contr. Load resistance : | 32.65 | Ohm |  |  |  |  | 13 | 0.31902 | 0.24685 | 0.39118
System voltage | 229 | V-rms |  | System voltage | 229 | V-rms |  |  |  |  | 15 | 0.31895 | 0.24678 | 0.39112
Volt-pk | 323.8549 | V-pk |  | Volt-pk | 323.8549 | V-pk |  |  |  |  | 17 | 0.24818 | 0.17602 | 0.32035
|  |  |  | Pwr | 5089.5007 | Watts |  |  |  |  | 19 | 0.24811 | 0.17595 | 0.32028
|  |  |  | VA | 5127.0308 | [5 empty] | 21 | 0.20312 | 0.13095 | 0.27528
|  |  |  | PF | 0.99268 |  | I-THC Limits in % |  |  |  | 23 | 0.20305 | 0.13088 | 0.27521
|  |  |  | I -Cr. Fact | 1.4844 |  | Table-2 | Table-3 | Table-4 | Table-5 | 25 | 0.17192 | 0.099757 | 0.24409
Start Phase | Stop Phase |  |  | I - THC in % | 11.8709 |  | 23 | 13 | 13 | 13 | 27 | 0.17186 | 0.099689 | 0.24402
45 | 135 | Degrees |  | I-THC in Amp | 2.6578 |  | PWHC Limits in % |  |  |  | 29 | 0.14906 | 0.076891 | 0.22122
0.7854 | 2.3562 | <-- Rad |  | PWHC in % | 14.5806 |  | 23 | 22 | 48 | 36 | 31 | 0.14899 | 0.076823 | 0.22116
|  |  |  | Current | 22.3889 | A-rms |  |  |  |  | 33 | 0.13158 | 0.059412 | 0.20375
|  |  |  | Amp-pk | 33.233 | A-pk |  |  |  |  | 35 | 0.13151 | 0.059343 | 0.20368
[11 empty] | 37 | 0.11778 | 0.045618 | 0.18995
|  |  |  | Start Phase | Stop Phase | [5 empty] | 39 | 0.11772 | 0.04555 | 0.18988
|  |  |  | 45 | 135 | Degrees
[18 empty] | Limits in A-rms |  |  |  |  | Table-2 Limits for Rsce 33 - 350 | [5 empty] | Table-3 Limits for Rsce 33 - 350
[18 empty] | Table 2 | Table-3 | Table-4 | Table-5 |  | 33 | 66 | 120 | 250 | 350 |  | 33 | 66 | 120 | 250 | 350
phase incr. | 0.006136 | [5 empty] | Current | [7 empty] | Angle
angle | V-t | A-t | P-t | On/Off | Ramp | On-Off | Flow |  |  |  | Harm. no | Amplitude | Real | Imaginary | degrees |  | I-THC ->> | 23 | 13 | 13 | 13 |  | 23 | 26 | 30 | 40 | 47 |  | 13 | 16 | 22 | 37 | 48
0 | 0 | 0 | 0 | FALSE | FALSE | FALSE | 0 |  |  |  | 0 | 7.0361e-07 | 0 | 7.0361e-07 | 0 |  | PWHC ->> | 23 | 22 | 48 | 36 |  | 23 | 26 | 30 | 40 | 47 |  | 22 | 25 | 28 | 38 | 46
0.006136 | 1.9872 | 0.060853 | 0.28429 | FALSE | FALSE | FALSE | 0.14306 |  |  |  | 1 | 22.2249 | 22.2249 | 0.013561 | 0.03496 | [6 empty] | Harm no
0.012272 | 3.9742 | 0.1217 | 1.1371 | FALSE | FALSE | FALSE | 0.28612 |  |  |  | 2 | 9.6865e-05 | 9.6852e-05 | 1.5861e-06 | 0 | 1.8766e-08 | 9.3829e-09 | 1.7911 | 1.7911 | 1.7911 | 1.7911 | 2 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8
0.018408 | 5.9612 | 0.18255 | 2.5583 | FALSE | FALSE | FALSE | 0.42917 |  |  |  | 3 | 2.2322 | -2.2321 | -0.013558 | -179.652 | 14.9478 | 4.9826 | 4.836 | 7.1868 | 7.1868 | 7.1868 | 3 | 21.6 | 24 | 27 | 36 | 41 |  | 32.1 | 42 | 57 | 93 | 120
0.024544 | 7.9479 | 0.24339 | 4.5477 | FALSE | FALSE | FALSE | 0.5722 |  |  |  | 4 | 1.292e-06 | 8.9392e-09 | 1.292e-06 | 0 | 6.6772e-12 | 1.6693e-12 | 0.89556 | 0.89556 | 0.89556 | 0.89556 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4
0.03068 | 9.9343 | 0.30422 | 7.105 | FALSE | FALSE | FALSE | 0.7152 |  |  |  | 5 | 0.74414 | -0.74402 | -0.013559 | -178.9559 | 2.7687 | 0.55375 | 2.3956 | 2.3956 | 2.3956 | 2.3956 | 5 | 10.7 | 13 | 15 | 20 | 24 |  | 10.7 | 14 | 19 | 31 | 40
0.036816 | 11.9203 | 0.36504 | 10.2298 | FALSE | FALSE | FALSE | 0.85819 |  |  |  | 6 | 9.6829e-05 | -9.6826e-05 | -7.6719e-07 | 0 | 5.6256e-08 | 9.3759e-09 | 0.59711 | 0.59711 | 0.59711 | 0.59711 | 6 | 2.667 | 2.667 | 2.667 | 2.667 | 2.667 |  | 2.667 | 2.667 | 2.667 | 2.667 | 2.667
0.042952 | 13.9059 | 0.42584 | 13.9217 | FALSE | FALSE | FALSE | 1.0011 |  |  |  | 7 | 0.74407 | 0.74395 | 0.01356 | 1.0442 | 3.8755 | 0.55365 | 1.612 | 1.612 | 1.612 | 1.612 | 7 | 7.2 | 8 | 10 | 13 | 15 |  | 7.2 | 9 | 12 | 20 | 25
0.049088 | 15.891 | 0.48663 | 18.18 | FALSE | FALSE | FALSE | 1.144 |  |  |  | 8 | 7.0363e-07 | 1.543e-08 | 7.0346e-07 | 0 | 3.9608e-12 | 4.9509e-13 | 0.44778 | 0.44778 | 0.44778 | 0.44778 | 8 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2
0.055224 | 17.8754 | 0.5474 | 23.0042 | FALSE | FALSE | FALSE | 1.2869 |  |  |  | 9 | 0.44654 | 0.44634 | 0.013562 | 1.7404 | 1.7946 | 0.1994 | 0.85078 | 0.69406 | 0.69406 | 0.69406 | 9 | 3.8 | 5 | 6 | 9 | 12 |  | 3.1 | 5 | 7 | 12 | 15
0.06136 | 19.8592 | 0.60815 | 28.3934 | FALSE | FALSE | FALSE | 1.4297 |  |  |  | 10 | 9.6921e-05 | 9.6841e-05 | 3.9394e-06 | 0 | 9.3937e-08 | 9.3937e-09 | 0.35822 | 0.35822 | 0.35822 | 0.35822 | 10 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 |  | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
0.067496 | 21.8423 | 0.66888 | 34.347 | FALSE | FALSE | FALSE | 1.5725 |  |  |  | 11 | 0.44648 | -0.44627 | -0.013558 | -178.2599 | 2.1927 | 0.19934 | 0.69406 | 0.69406 | 0.69406 | 0.69406 | 11 | 3.1 | 4 | 5 | 8 | 10 |  | 3.1 | 5 | 7 | 12 | 15
0.073632 | 23.8245 | 0.72958 | 40.8639 | FALSE | FALSE | FALSE | 1.7152 |  |  |  | 12 | 1.2925e-06 | 2.6817e-08 | 1.2923e-06 | 0 | 2.0048e-11 | 1.6707e-12 | 0.29844 | 0.29844 | 0.29844 | 0.29844 | 12 | 1.333 | 1.333 | 1.333 | 1.333 | 1.333 |  | 1.333 | 1.333 | 1.333 | 1.333 | 1.333
0.079768 | 25.8058 | 0.79026 | 47.9433 | FALSE | FALSE | FALSE | 1.8579 |  |  |  | 13 | 0.31902 | -0.31873 | -0.01356 | -177.5639 | 1.323 | 0.10177 | 0.44778 | 0.44778 | 0.44778 | 0.44778 | 13 | 2 | 3 | 4 | 6 | 8 |  | 2 | 3 | 4 | 7 | 10
0.085904 | 27.7862 | 0.8509 | 55.5841 | FALSE | FALSE | FALSE | 2.0004 |  |  |  | 14 | 9.6813e-05 | -9.6762e-05 | -3.1205e-06 | 0 | 1.3122e-07 | 9.3727e-09 |  |  |  | 0.22389 |  | Table-4 Limits for Rsce 33 - 350 | [5 empty] | Table-5 Limits for Rsce 33 - 350
0.09204 | 29.7655 | 0.91151 | 63.785 | FALSE | FALSE | FALSE | 2.1429 |  |  |  | 15 | 0.31895 | 0.31866 | 0.013559 | 2.4365 | 1.5259 | 0.10173 |  |  |  | 0.33583 |  | 33 | 66 | 120 | 250 | 350 |  | 33 | 66 | 120 | 250 | 350
0.098176 | 31.7436 | 0.97209 | 72.5449 | FALSE | FALSE | FALSE | 2.2853 |  |  |  | 16 | 7.0368e-07 | 3.0877e-08 | 7.03e-07 | 0 | 7.9227e-12 | 4.9517e-13 |  |  |  | 0.22389 |  | 13 | 13 | 22 | 22 | 22 |  | 13 | 13 | 13 | 22 | 22
0.10431 | 33.7206 | 1.0326 | 81.8625 | FALSE | FALSE | FALSE | 2.4277 |  |  |  | 17 | 0.24818 | 0.24781 | 0.013563 | 3.1326 | 1.0471 | 0.061594 |  |  |  | 0.44778 |  | 48 | 48 | 46 | 46 | 46 |  | 36 | 36 | 36 | 70 | 70
0.11045 | 35.6963 | 1.0931 | 91.7363 | FALSE | FALSE | FALSE | 2.5699 |  |  |  | 18 | 9.6996e-05 | 9.6791e-05 | 6.2927e-06 | 0 | 1.6935e-07 | 9.4082e-09 |  |  |  | 0.22389 | Harm no | [5 empty] | Harm no
0.11658 | 37.6707 | 1.1536 | 102.1649 | FALSE | FALSE | FALSE | 2.712 |  |  |  | 19 | 0.24811 | -0.24774 | -0.013557 | -176.8678 | 1.1696 | 0.06156 |  |  |  | 0.33583 | 2 | 8 | 8 | 8 | 8 | 8 | 2 | 8 | 8 | 8 | 8 | 8
0.12272 | 39.6437 | 1.214 | 113.1466 | FALSE | FALSE | FALSE | 2.8541 |  |  |  | 20 | 1.2936e-06 | 4.4693e-08 | 1.2928e-06 | 0 | 3.3468e-11 | 1.6734e-12 |  |  |  | 0.22389 | 3 | 32.1 | 32.1 | 120 | 120 | 120 | 3 | 32.1 | 32.1 | 32.1 | 75 | 75
0.12886 | 41.6151 | 1.2744 | 124.6799 | FALSE | FALSE | FALSE | 2.996 |  |  |  | 21 | 0.20312 | -0.20266 | -0.013561 | -176.1718 | 0.86637 | 0.041256 |  |  |  | 0.33583 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
0.13499 | 43.585 | 1.3347 | 136.763 | FALSE | FALSE | FALSE | 3.1378 |  |  |  | 22 | 9.6816e-05 | -9.6661e-05 | -5.4739e-06 | 0 | 2.0621e-07 | 9.3733e-09 |  |  |  | 0.22389 | 5 | 10.7 | 10.7 | 40 | 40 | 40 | 5 | 10.7 | 10.7 | 10.7 | 25 | 25
0.14113 | 45.5533 | 1.395 | 149.3941 | FALSE | FALSE | FALSE | 3.2795 |  |  |  | 23 | 0.20305 | 0.20259 | 0.013558 | 3.8288 | 0.94825 | 0.041228 |  |  |  | 0.33583 | 6 | 2.667 | 2.667 | 2.667 | 2.667 | 2.667 | 6 | 2.667 | 2.667 | 2.667 | 2.667 | 2.667
0.14726 | 47.5198 | 1.4552 | 162.5712 | FALSE | FALSE | FALSE | 3.4211 |  |  |  | 24 | 7.0377e-07 | 4.6358e-08 | 7.0224e-07 | 0 | 1.1887e-11 | 4.9529e-13 |  |  |  | 0.22389 | 7 | 7.2 | 7.2 | 25 | 25 | 25 | 7 | 7.2 | 7.2 | 7.2 | 17.3 | 17.3
0.1534 | 49.4846 | 1.5154 | 176.2924 | FALSE | FALSE | FALSE | 3.5626 |  |  |  | 25 | 0.17192 | 0.17139 | 0.013564 | 4.5249 | 0.73895 | 0.029558 |  |  |  | 0.33583 | 8 | 2 | 2 | 2 | 2 | 2 | 8 | 2 | 2 | 2 | 2 | 2
0.15954 | 51.4475 | 1.5755 | 190.5557 | FALSE | FALSE | FALSE | 3.7039 |  |  |  | 26 | 9.709e-05 | 9.6704e-05 | 8.6461e-06 | 0 | 2.4509e-07 | 9.4265e-09 |  |  |  | 0.22389 | 9 | 3.1 | 3.1 | 15 | 15 | 15 | 9 | 3.1 | 3.1 | 3.1 | 12.1 | 12.1
0.16567 | 53.4084 | 1.6355 | 205.3588 | FALSE | FALSE | FALSE | 3.8451 |  |  |  | 27 | 0.17186 | -0.17132 | -0.013556 | -175.4757 | 0.79742 | 0.029534 |  |  |  | 0.22389 | 10 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 10 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
0.17181 | 55.3674 | 1.6955 | 220.6996 | FALSE | FALSE | FALSE | 3.9861 |  |  |  | 28 | 1.2952e-06 | 6.2564e-08 | 1.2937e-06 | 0 | 4.6969e-11 | 1.6775e-12 |  |  |  | 0.22389 | 11 | 3.1 | 3.1 | 15 | 15 | 15 | 11 | 3.1 | 3.1 | 3.1 | 12.1 | 12.1
0.17794 | 57.3242 | 1.7555 | 236.5757 | FALSE | FALSE | FALSE | 4.127 |  |  |  | 29 | 0.14906 | -0.14844 | -0.013562 | -174.7797 | 0.64433 | 0.022218 |  |  |  | 0.22389 | 12 | 1.333 | 1.333 | 1.333 | 1.333 | 1.333 | 12 | 1.333 | 1.333 | 1.333 | 1.333 | 1.333
0.18408 | 59.2789 | 1.8153 | 252.9848 | FALSE | FALSE | FALSE | 4.2677 |  |  |  | 30 | 9.6838e-05 | -9.6521e-05 | -7.8274e-06 | 0 | 2.8133e-07 | 9.3777e-09 |  |  |  | 0.22389 | 13 | 2 | 2 | 10 | 10 | 10 | 13 | 2 | 2 | 2 | 10.7 | 10.7
0.19022 | 61.2314 | 1.8751 | 269.9243 | FALSE | FALSE | FALSE | 4.4083 |  |  |  | 31 | 0.14899 | 0.14837 | 0.013558 | 5.2211 | 0.68813 | 0.022198 |  |  |  | 0.22389 | [6 empty] | 14 | 1 | 1 | 1 | 3 | 3
0.19635 | 63.1816 | 1.9348 | 287.3918 | FALSE | FALSE | FALSE | 4.5487 |  |  |  | 32 | 7.039e-07 | 6.1891e-08 | 7.0118e-07 | 0 | 1.5855e-11 | 4.9548e-13 |  |  |  | 0.22389 | [6 empty] | 15 | 1.5 | 1.5 | 1.5 | 8.4 | 8.4
0.20249 | 65.1293 | 1.9945 | 305.3846 | FALSE | FALSE | FALSE | 4.6889 |  |  |  | 33 | 0.13158 | 0.13088 | 0.013565 | 5.9172 | 0.57133 | 0.017313 |  |  |  | 0.22389 | [6 empty] | 16 | 1 | 1 | 1 | 3 | 3
0.20862 | 67.0747 | 2.054 | 323.8999 | FALSE | FALSE | FALSE | 4.8289 |  |  |  | 34 | 9.7204e-05 | 9.6579e-05 | 1.0999e-05 | 0 | 3.2125e-07 | 9.4485e-09 |  |  |  | 0.22389 | [6 empty] | 17 | 2 | 2 | 2 | 8.4 | 8.4
0.21476 | 69.0175 | 2.1135 | 342.935 | FALSE | FALSE | FALSE | 4.9688 |  |  |  | 35 | 0.13151 | -0.13081 | -0.013556 | -174.0837 | 0.60532 | 0.017295 |  |  |  | 0.22389 | [6 empty] | 18 | 1 | 1 | 1 | 3 | 3
0.2209 | 70.9577 | 2.173 | 362.4871 | FALSE | FALSE | FALSE | 5.1085 |  |  |  | 36 | 1.2973e-06 | 8.0431e-08 | 1.2948e-06 | 0 | 6.0586e-11 | 1.6829e-12 |  |  |  | 0.22389 | [6 empty] | 19 | 1.5 | 1.5 | 1.5 | 7.8 | 7.8
0.22703 | 72.8952 | 2.2323 | 382.5532 | FALSE | FALSE | FALSE | 5.248 |  |  |  | 37 | 0.11778 | -0.117 | -0.013563 | -173.3876 | 0.51331 | 0.013873 |  |  |  | 0.22389 | [6 empty] | 20 | 1 | 1 | 1 | 3 | 3
0.23317 | 74.83 | 2.2915 | 403.1302 | FALSE | FALSE | FALSE | 5.3873 |  |  |  | 38 | 9.6881e-05 | -9.6344e-05 | -1.0181e-05 | 0 | 3.5666e-07 | 9.3858e-09 |  |  |  | 0.22389 | [6 empty] | 21 | 1.5 | 1.5 | 1.5 | 6.8 | 6.8
0.2393 | 76.762 | 2.3507 | 424.215 | FALSE | FALSE | FALSE | 5.5264 |  |  |  | 39 | 0.11772 | 0.11693 | 0.013557 | 6.6133 | 0.54043 | 0.013857 |  |  |  | 0.22389 | [6 empty] | 22 | 1 | 1 | 1 | 3 | 3
0.24544 | 78.6911 | 2.4098 | 445.8046 | FALSE | FALSE | FALSE | 5.6652 |  |  |  | 40 | 7.0408e-07 | 7.7492e-08 | 6.9981e-07 | 0 | 1.9829e-11 | 4.9573e-13 |  |  |  | 0.22389 | [6 empty] | 23 | 1.5 | 1.5 | 1.5 | 6.8 | 6.8
0.25158 | 80.6172 | 2.4688 | 467.8956 | FALSE | FALSE | FALSE | 5.8039 | [8 empty] | 3.2644 | 2.6578 | 0.49833 | [9 empty] | 24 | 1 | 1 | 1 | 3 | 3
0.25771 | 82.5403 | 2.5277 | 490.4847 | FALSE | FALSE | FALSE | 5.9424 | [9 empty] | THC-I | POHC | [9 empty] | 25 | 1.5 | 1.5 | 1.5 | 6.5 | 6.5
0.26385 | 84.4603 | 2.5864 | 513.5685 | FALSE | FALSE | FALSE | 6.0806 | [20 empty] | 26 | 1 | 1 | 1 | 3 | 3
0.26998 | 86.3771 | 2.6451 | 537.1436 | FALSE | FALSE | FALSE | 6.2186 | [20 empty] | 27 | 1 | 1 | 1 | 5.4 | 5.4
0.27612 | 88.2906 | 2.7037 | 561.2063 | FALSE | FALSE | FALSE | 6.3564 | [20 empty] | 28 | 1 | 1 | 1 | 3 | 3
0.28226 | 90.2008 | 2.7622 | 585.7531 | FALSE | FALSE | FALSE | 6.4939 | [20 empty] | 29 | 1 | 1 | 1 | 5.4 | 5.4
0.28839 | 92.1077 | 2.8206 | 610.7803 | FALSE | FALSE | FALSE | 6.6312 | [20 empty] | 30 | 1 | 1 | 1 | 3 | 3
0.29453 | 94.011 | 2.8789 | 636.284 | FALSE | FALSE | FALSE | 6.7682 | [20 empty] | 31 | 1 | 1 | 1 | 5.2 | 5.2
0.30066 | 95.9108 | 2.9371 | 662.2605 | FALSE | FALSE | FALSE | 6.905 | [20 empty] | 32 | 1 | 1 | 1 | 3 | 3
0.3068 | 97.807 | 2.9952 | 688.7058 | FALSE | FALSE | FALSE | 7.0415 | [20 empty] | 33 | 1 | 1 | 1 | 5.2 | 5.2
0.31294 | 99.6996 | 3.0531 | 715.616 | FALSE | FALSE | FALSE | 7.1777 | [20 empty] | 34 | 1 | 1 | 1 | 3 | 3
0.31907 | 101.5883 | 3.111 | 742.987 | FALSE | FALSE | FALSE | 7.3137 | [20 empty] | 35 | 1 | 1 | 1 | 4.9 | 4.9
0.32521 | 103.4733 | 3.1687 | 770.8147 | FALSE | FALSE | FALSE | 7.4494 | [20 empty] | 36 | 1 | 1 | 1 | 3 | 3
0.33134 | 105.3543 | 3.2263 | 799.0948 | FALSE | FALSE | FALSE | 7.5848 | [20 empty] | 37 | 1 | 1 | 1 | 4.7 | 4.7
0.33748 | 107.2314 | 3.2838 | 827.8232 | FALSE | FALSE | FALSE | 7.72 | [20 empty] | 38 | 1 | 1 | 1 | 3 | 3
0.34362 | 109.1045 | 3.3411 | 856.9955 | FALSE | FALSE | FALSE | 7.8548 | [20 empty] | 39 | 1 | 1 | 1 | 4.7 | 4.7
0.34975 | 110.9734 | 3.3984 | 886.6073 | FALSE | FALSE | FALSE | 7.9894 | [20 empty] | 40 | 1 | 1 | 1 | 3 | 3
0.35589 | 112.8382 | 3.4555 | 916.6542 | FALSE | FALSE | FALSE | 8.1236
0.36202 | 114.6987 | 3.5124 | 947.1316 | FALSE | FALSE | FALSE | 8.2576
0.36816 | 116.5549 | 3.5693 | 978.0349 | FALSE | FALSE | FALSE | 8.3912
0.37429 | 118.4067 | 3.626 | 1009.3595 | FALSE | FALSE | FALSE | 8.5245
0.38043 | 120.254 | 3.6826 | 1041.1007 | FALSE | FALSE | FALSE | 8.6575
0.38657 | 122.0968 | 3.739 | 1073.2537 | FALSE | FALSE | FALSE | 8.7902
0.3927 | 123.9351 | 3.7953 | 1105.8136 | FALSE | FALSE | FALSE | 8.9225
0.39884 | 125.7686 | 3.8514 | 1138.7755 | FALSE | FALSE | FALSE | 9.0545
0.40497 | 127.5974 | 3.9074 | 1172.1345 | FALSE | FALSE | FALSE | 9.1862 |  |  |  | 33
0.41111 | 129.4214 | 3.9633 | 1205.8856 | FALSE | FALSE | FALSE | 9.3175
0.41725 | 131.2406 | 4.019 | 1240.0236 | FALSE | FALSE | FALSE | 9.4485
0.42338 | 133.0548 | 4.0746 | 1274.5435 | FALSE | FALSE | FALSE | 9.5791
0.42952 | 134.864 | 4.13 | 1309.44 | FALSE | FALSE | FALSE | 9.7093 |  |  |  | 35
0.43565 | 136.6681 | 4.1852 | 1344.7079 | FALSE | FALSE | FALSE | 9.8392
0.44179 | 138.4671 | 4.2403 | 1380.3418 | FALSE | FALSE | FALSE | 9.9687
0.44793 | 140.2608 | 4.2952 | 1416.3364 | FALSE | FALSE | FALSE | 10.0979
0.45406 | 142.0493 | 4.35 | 1452.6863 | FALSE | FALSE | FALSE | 10.2266 |  |  |  | 37
0.4602 | 143.8324 | 4.4046 | 1489.386 | FALSE | FALSE | FALSE | 10.355
0.46633 | 145.6102 | 4.4591 | 1526.43 | FALSE | FALSE | FALSE | 10.483
0.47247 | 147.3824 | 4.5133 | 1563.8127 | FALSE | FALSE | FALSE | 10.6106
0.47861 | 149.1491 | 4.5674 | 1601.5284 | FALSE | FALSE | FALSE | 10.7378 |  |  |  | 39
0.48474 | 150.9101 | 4.6214 | 1639.5716 | FALSE | FALSE | FALSE | 10.8646
0.49088 | 152.6655 | 4.6751 | 1677.9364 | FALSE | FALSE | FALSE | 10.9909
0.49701 | 154.4152 | 4.7287 | 1716.617 | FALSE | FALSE | FALSE | 11.1169
0.50315 | 156.159 | 4.7821 | 1755.6077 | FALSE | FALSE | FALSE | 11.2424
0.50929 | 157.8969 | 4.8353 | 1794.9026 | FALSE | FALSE | FALSE | 11.3676
0.51542 | 159.6289 | 4.8884 | 1834.4958 | FALSE | FALSE | FALSE | 11.4923
0.52156 | 161.3549 | 4.9412 | 1874.3812 | FALSE | FALSE | FALSE | 11.6165
0.52769 | 163.0748 | 4.9939 | 1914.553 | FALSE | FALSE | FALSE | 11.7403
0.53383 | 164.7886 | 5.0464 | 1955.005 | FALSE | FALSE | FALSE | 11.8637
0.53997 | 166.4962 | 5.0987 | 1995.7311 | FALSE | FALSE | FALSE | 11.9866
0.5461 | 168.1975 | 5.1508 | 2036.7253 | FALSE | FALSE | FALSE | 12.1091
0.55224 | 169.8924 | 5.2027 | 2077.9813 | FALSE | FALSE | FALSE | 12.2312
0.55837 | 171.581 | 5.2544 | 2119.493 | FALSE | FALSE | FALSE | 12.3527
0.56451 | 173.2631 | 5.3059 | 2161.254 | FALSE | FALSE | FALSE | 12.4738
0.57065 | 174.9387 | 5.3572 | 2203.2581 | FALSE | FALSE | FALSE | 12.5945
0.57678 | 176.6077 | 5.4083 | 2245.499 | FALSE | FALSE | FALSE | 12.7146
0.58292 | 178.2701 | 5.4592 | 2287.9703 | FALSE | FALSE | FALSE | 12.8343
0.58905 | 179.9257 | 5.5099 | 2330.6656 | FALSE | FALSE | FALSE | 12.9535
0.59519 | 181.5746 | 5.5604 | 2373.5785 | FALSE | FALSE | FALSE | 13.0722
0.60133 | 183.2166 | 5.6107 | 2416.7025 | FALSE | FALSE | FALSE | 13.1904
0.60746 | 184.8517 | 5.6608 | 2460.0311 | FALSE | FALSE | FALSE | 13.3081
0.6136 | 186.4799 | 5.7106 | 2503.5578 | FALSE | FALSE | FALSE | 13.4253
0.61973 | 188.101 | 5.7603 | 2547.276 | FALSE | FALSE | FALSE | 13.5421
0.62587 | 189.7151 | 5.8097 | 2591.1792 | FALSE | FALSE | FALSE | 13.6583
0.63201 | 191.322 | 5.8589 | 2635.2608 | FALSE | FALSE | FALSE | 13.774
0.63814 | 192.9218 | 5.9079 | 2679.514 | FALSE | FALSE | FALSE | 13.8891
0.64428 | 194.5142 | 5.9567 | 2723.9323 | FALSE | FALSE | FALSE | 14.0038
0.65041 | 196.0994 | 6.0052 | 2768.509 | FALSE | FALSE | FALSE | 14.1179
0.65655 | 197.6771 | 6.0535 | 2813.2373 | FALSE | FALSE | FALSE | 14.2315
0.66269 | 199.2474 | 6.1016 | 2858.1104 | FALSE | FALSE | FALSE | 14.3445
0.66882 | 200.8102 | 6.1495 | 2903.1218 | FALSE | FALSE | FALSE | 14.457
0.67496 | 202.3655 | 6.1971 | 2948.2645 | FALSE | FALSE | FALSE | 14.569
0.68109 | 203.9131 | 6.2445 | 2993.5318 | FALSE | FALSE | FALSE | 14.6804
0.68723 | 205.4531 | 6.2916 | 3038.9168 | FALSE | FALSE | FALSE | 14.7913
0.69337 | 206.9853 | 6.3386 | 3084.4127 | FALSE | FALSE | FALSE | 14.9016
0.6995 | 208.5097 | 6.3852 | 3130.0127 | FALSE | FALSE | FALSE | 15.0114
0.70564 | 210.0263 | 6.4317 | 3175.7099 | FALSE | FALSE | FALSE | 15.1205
0.71177 | 211.5349 | 6.4779 | 3221.4974 | FALSE | FALSE | FALSE | 15.2292
0.71791 | 213.0356 | 6.5238 | 3267.3684 | FALSE | FALSE | FALSE | 15.3372
0.72405 | 214.5283 | 6.5696 | 3313.3158 | FALSE | FALSE | FALSE | 15.4447
0.73018 | 216.0129 | 6.615 | 3359.3328 | FALSE | FALSE | FALSE | 15.5515
0.73632 | 217.4894 | 6.6602 | 3405.4125 | FALSE | FALSE | FALSE | 15.6578
0.74245 | 218.9577 | 6.7052 | 3451.5479 | FALSE | FALSE | FALSE | 15.7635
0.74859 | 220.4177 | 6.7499 | 3497.7321 | FALSE | FALSE | FALSE | 15.8687
0.75473 | 221.8694 | 6.7944 | 3543.9582 | FALSE | FALSE | FALSE | 15.9732
0.76086 | 223.3128 | 6.8386 | 3590.219 | FALSE | FALSE | FALSE | 16.0771
0.767 | 224.7478 | 6.8825 | 3636.5078 | FALSE | FALSE | FALSE | 16.1804
0.77313 | 226.1743 | 6.9262 | 3682.8175 | FALSE | FALSE | FALSE | 16.2831
0.77927 | 227.5923 | 6.9696 | 3729.1411 | FALSE | FALSE | FALSE | 16.3852
0.78541 | 229.0018 | 7.0128 | 5381.41 | TRUE | FALSE | TRUE | 23.4994
0.79154 | 230.4026 | 7.0557 | 5447.4478 | TRUE | FALSE | TRUE | 23.6432
0.79768 | 231.7947 | 7.0983 | 5513.4756 | TRUE | FALSE | TRUE | 23.786
0.80381 | 233.1781 | 7.1407 | 5579.4836 | TRUE | FALSE | TRUE | 23.928
0.80995 | 234.5527 | 7.1828 | 5645.4617 | TRUE | FALSE | TRUE | 24.0691
0.81609 | 235.9185 | 7.2246 | 5711.4 | TRUE | FALSE | TRUE | 24.2092
0.82222 | 237.2754 | 7.2661 | 5777.2886 | TRUE | FALSE | TRUE | 24.3484
0.82836 | 238.6234 | 7.3074 | 5843.1176 | TRUE | FALSE | TRUE | 24.4868
0.83449 | 239.9624 | 7.3484 | 5908.877 | TRUE | FALSE | TRUE | 24.6242
0.84063 | 241.2924 | 7.3892 | 5974.557 | TRUE | FALSE | TRUE | 24.7607
0.84677 | 242.6133 | 7.4296 | 6040.1477 | TRUE | FALSE | TRUE | 24.8962
0.8529 | 243.925 | 7.4698 | 6105.6391 | TRUE | FALSE | TRUE | 25.0308
0.85904 | 245.2276 | 7.5097 | 6171.0214 | TRUE | FALSE | TRUE | 25.1645
0.86517 | 246.5209 | 7.5493 | 6236.2849 | TRUE | FALSE | TRUE | 25.2972
0.87131 | 247.8049 | 7.5886 | 6301.4195 | TRUE | FALSE | TRUE | 25.4289
0.87745 | 249.0797 | 7.6276 | 6366.4156 | TRUE | FALSE | TRUE | 25.5598
0.88358 | 250.345 | 7.6664 | 6431.2634 | TRUE | FALSE | TRUE | 25.6896
0.88972 | 251.6009 | 7.7048 | 6495.953 | TRUE | FALSE | TRUE | 25.8185
0.89585 | 252.8474 | 7.743 | 6560.4748 | TRUE | FALSE | TRUE | 25.9464
0.90199 | 254.0843 | 7.7809 | 6624.819 | TRUE | FALSE | TRUE | 26.0733
0.90813 | 255.3116 | 7.8185 | 6688.9759 | TRUE | FALSE | TRUE | 26.1993
0.91426 | 256.5294 | 7.8558 | 6752.9359 | TRUE | FALSE | TRUE | 26.3242
0.9204 | 257.7374 | 7.8928 | 6816.6893 | TRUE | FALSE | TRUE | 26.4482
0.92653 | 258.9358 | 7.9295 | 6880.2266 | TRUE | FALSE | TRUE | 26.5712
0.93267 | 260.1245 | 7.9659 | 6943.5381 | TRUE | FALSE | TRUE | 26.6931
0.93881 | 261.3033 | 8.002 | 7006.6144 | TRUE | FALSE | TRUE | 26.8141
0.94494 | 262.4723 | 8.0378 | 7069.4459 | TRUE | FALSE | TRUE | 26.9341
0.95108 | 263.6314 | 8.0732 | 7132.0231 | TRUE | FALSE | TRUE | 27.053
0.95721 | 264.7806 | 8.1084 | 7194.3367 | TRUE | FALSE | TRUE | 27.1709
0.96335 | 265.9198 | 8.1433 | 7256.3773 | TRUE | FALSE | TRUE | 27.2878
0.96949 | 267.049 | 8.1779 | 7318.1355 | TRUE | FALSE | TRUE | 27.4037
0.97562 | 268.1682 | 8.2122 | 7379.602 | TRUE | FALSE | TRUE | 27.5186
0.98176 | 269.2772 | 8.2461 | 7440.7676 | TRUE | FALSE | TRUE | 27.6324
0.98789 | 270.3762 | 8.2798 | 7501.623 | TRUE | FALSE | TRUE | 27.7451
0.99403 | 271.4649 | 8.3131 | 7562.1591 | TRUE | FALSE | TRUE | 27.8569
1.0002 | 272.5434 | 8.3462 | 7622.3668 | TRUE | FALSE | TRUE | 27.9675
1.0063 | 273.6117 | 8.3789 | 7682.237 | TRUE | FALSE | TRUE | 28.0772
1.0124 | 274.6696 | 8.4113 | 7741.7606 | TRUE | FALSE | TRUE | 28.1857
1.0186 | 275.7172 | 8.4434 | 7800.9288 | TRUE | FALSE | TRUE | 28.2932
1.0247 | 276.7545 | 8.4751 | 7859.7326 | TRUE | FALSE | TRUE | 28.3997
1.0308 | 277.7813 | 8.5066 | 7918.1631 | TRUE | FALSE | TRUE | 28.505
1.037 | 278.7977 | 8.5377 | 7976.2116 | TRUE | FALSE | TRUE | 28.6093
1.0431 | 279.8035 | 8.5685 | 8033.8694 | TRUE | FALSE | TRUE | 28.7125
1.0493 | 280.7988 | 8.599 | 8091.1276 | TRUE | FALSE | TRUE | 28.8147
1.0554 | 281.7836 | 8.6291 | 8147.9777 | TRUE | FALSE | TRUE | 28.9157
1.0615 | 282.7577 | 8.659 | 8204.4112 | TRUE | FALSE | TRUE | 29.0157
1.0677 | 283.7212 | 8.6885 | 8260.4196 | TRUE | FALSE | TRUE | 29.1146
1.0738 | 284.674 | 8.7176 | 8315.9943 | TRUE | FALSE | TRUE | 29.2123
1.0799 | 285.6161 | 8.7465 | 8371.1271 | TRUE | FALSE | TRUE | 29.309
1.0861 | 286.5475 | 8.775 | 8425.8096 | TRUE | FALSE | TRUE | 29.4046
1.0922 | 287.468 | 8.8032 | 8480.0337 | TRUE | FALSE | TRUE | 29.499
1.0983 | 288.3778 | 8.8311 | 8533.791 | TRUE | FALSE | TRUE | 29.5924
1.1045 | 289.2766 | 8.8586 | 8587.0736 | TRUE | FALSE | TRUE | 29.6846
1.1106 | 290.1646 | 8.8858 | 8639.8735 | TRUE | FALSE | TRUE | 29.7758
1.1167 | 291.0417 | 8.9126 | 8692.1826 | TRUE | FALSE | TRUE | 29.8658
1.1229 | 291.9078 | 8.9392 | 8743.993 | TRUE | FALSE | TRUE | 29.9546
1.129 | 292.7629 | 8.9654 | 8795.2971 | TRUE | FALSE | TRUE | 30.0424
1.1352 | 293.607 | 8.9912 | 8846.087 | TRUE | FALSE | TRUE | 30.129
1.1413 | 294.44 | 9.0167 | 8896.3552 | TRUE | FALSE | TRUE | 30.2145
1.1474 | 295.262 | 9.0419 | 8946.0939 | TRUE | FALSE | TRUE | 30.2988
1.1536 | 296.0728 | 9.0667 | 8995.2959 | TRUE | FALSE | TRUE | 30.382
1.1597 | 296.8725 | 9.0912 | 9043.9535 | TRUE | FALSE | TRUE | 30.4641
1.1658 | 297.661 | 9.1153 | 9092.0596 | TRUE | FALSE | TRUE | 30.545
1.172 | 298.4383 | 9.1391 | 9139.6068 | TRUE | FALSE | TRUE | 30.6248
1.1781 | 299.2043 | 9.1626 | 9186.5881 | TRUE | FALSE | TRUE | 30.7034
1.1842 | 299.9591 | 9.1857 | 9232.9962 | TRUE | FALSE | TRUE | 30.7808
1.1904 | 300.7026 | 9.2085 | 9278.8244 | TRUE | FALSE | TRUE | 30.8571
1.1965 | 301.4348 | 9.2309 | 9324.0655 | TRUE | FALSE | TRUE | 30.9323
1.2027 | 302.1557 | 9.253 | 9368.7129 | TRUE | FALSE | TRUE | 31.0062
1.2088 | 302.8651 | 9.2747 | 9412.7598 | TRUE | FALSE | TRUE | 31.079
1.2149 | 303.5632 | 9.2961 | 9456.1995 | TRUE | FALSE | TRUE | 31.1507
1.2211 | 304.2498 | 9.3171 | 9499.0256 | TRUE | FALSE | TRUE | 31.2211
1.2272 | 304.925 | 9.3378 | 9541.2316 | TRUE | FALSE | TRUE | 31.2904
1.2333 | 305.5887 | 9.3581 | 9582.8111 | TRUE | FALSE | TRUE | 31.3585
1.2395 | 306.2408 | 9.3781 | 9623.7578 | TRUE | FALSE | TRUE | 31.4255
1.2456 | 306.8815 | 9.3977 | 9664.0656 | TRUE | FALSE | TRUE | 31.4912
1.2517 | 307.5106 | 9.417 | 9703.7285 | TRUE | FALSE | TRUE | 31.5558
1.2579 | 308.1281 | 9.4359 | 9742.7404 | TRUE | FALSE | TRUE | 31.6191
1.264 | 308.734 | 9.4544 | 9781.0955 | TRUE | FALSE | TRUE | 31.6813
1.2701 | 309.3283 | 9.4726 | 9818.788 | TRUE | FALSE | TRUE | 31.7423
1.2763 | 309.911 | 9.4905 | 9855.8122 | TRUE | FALSE | TRUE | 31.8021
1.2824 | 310.482 | 9.508 | 9892.1625 | TRUE | FALSE | TRUE | 31.8607
1.2886 | 311.0413 | 9.5251 | 9927.8335 | TRUE | FALSE | TRUE | 31.9181
1.2947 | 311.5889 | 9.5419 | 9962.8198 | TRUE | FALSE | TRUE | 31.9742
1.3008 | 312.1247 | 9.5583 | 9997.1162 | TRUE | FALSE | TRUE | 32.0292
1.307 | 312.6488 | 9.5743 | 10030.7174 | TRUE | FALSE | TRUE | 32.083
1.3131 | 313.1611 | 9.59 | 10063.6184 | TRUE | FALSE | TRUE | 32.1356
1.3192 | 313.6617 | 9.6053 | 10095.8143 | TRUE | FALSE | TRUE | 32.187
1.3254 | 314.1504 | 9.6203 | 10127.3002 | TRUE | FALSE | TRUE | 32.2371
1.3315 | 314.6273 | 9.6349 | 10158.0713 | TRUE | FALSE | TRUE | 32.286
1.3376 | 315.0924 | 9.6492 | 10188.123 | TRUE | FALSE | TRUE | 32.3338
1.3438 | 315.5455 | 9.663 | 10217.4509 | TRUE | FALSE | TRUE | 32.3803
1.3499 | 315.9869 | 9.6765 | 10246.0504 | TRUE | FALSE | TRUE | 32.4256
1.3561 | 316.4163 | 9.6897 | 10273.9174 | TRUE | FALSE | TRUE | 32.4696
1.3622 | 316.8338 | 9.7025 | 10301.0474 | TRUE | FALSE | TRUE | 32.5125
1.3683 | 317.2393 | 9.7149 | 10327.4366 | TRUE | FALSE | TRUE | 32.5541
1.3745 | 317.633 | 9.727 | 10353.0809 | TRUE | FALSE | TRUE | 32.5945
1.3806 | 318.0146 | 9.7386 | 10377.9765 | TRUE | FALSE | TRUE | 32.6336
1.3867 | 318.3843 | 9.75 | 10402.1196 | TRUE | FALSE | TRUE | 32.6716
1.3929 | 318.742 | 9.7609 | 10425.5065 | TRUE | FALSE | TRUE | 32.7083
1.399 | 319.0878 | 9.7715 | 10448.1338 | TRUE | FALSE | TRUE | 32.7438
1.4051 | 319.4214 | 9.7817 | 10469.9981 | TRUE | FALSE | TRUE | 32.778
1.4113 | 319.7431 | 9.7916 | 10491.096 | TRUE | FALSE | TRUE | 32.811
1.4174 | 320.0527 | 9.8011 | 10511.4243 | TRUE | FALSE | TRUE | 32.8428
1.4235 | 320.3503 | 9.8102 | 10530.9801 | TRUE | FALSE | TRUE | 32.8733
1.4297 | 320.6358 | 9.8189 | 10549.7603 | TRUE | FALSE | TRUE | 32.9026
1.4358 | 320.9093 | 9.8273 | 10567.7622 | TRUE | FALSE | TRUE | 32.9307
1.442 | 321.1707 | 9.8353 | 10584.983 | TRUE | FALSE | TRUE | 32.9575
1.4481 | 321.4199 | 9.8429 | 10601.4202 | TRUE | FALSE | TRUE | 32.9831
1.4542 | 321.6571 | 9.8502 | 10617.0712 | TRUE | FALSE | TRUE | 33.0074
1.4604 | 321.8822 | 9.8571 | 10631.9337 | TRUE | FALSE | TRUE | 33.0305
1.4665 | 322.0951 | 9.8636 | 10646.0054 | TRUE | FALSE | TRUE | 33.0524
1.4726 | 322.2959 | 9.8697 | 10659.2843 | TRUE | FALSE | TRUE | 33.073
1.4788 | 322.4846 | 9.8755 | 10671.7684 | TRUE | FALSE | TRUE | 33.0923
1.4849 | 322.6611 | 9.8809 | 10683.4557 | TRUE | FALSE | TRUE | 33.1105
1.491 | 322.8255 | 9.886 | 10694.3445 | TRUE | FALSE | TRUE | 33.1273
1.4972 | 322.9778 | 9.8906 | 10704.4332 | TRUE | FALSE | TRUE | 33.1429
1.5033 | 323.1178 | 9.8949 | 10713.7202 | TRUE | FALSE | TRUE | 33.1573
1.5095 | 323.2457 | 9.8988 | 10722.2042 | TRUE | FALSE | TRUE | 33.1704
1.5156 | 323.3615 | 9.9024 | 10729.8838 | TRUE | FALSE | TRUE | 33.1823
1.5217 | 323.465 | 9.9055 | 10736.7579 | TRUE | FALSE | TRUE | 33.1929
1.5279 | 323.5564 | 9.9083 | 10742.8256 | TRUE | FALSE | TRUE | 33.2023
1.534 | 323.6356 | 9.9108 | 10748.0857 | TRUE | FALSE | TRUE | 33.2105
1.5401 | 323.7027 | 9.9128 | 10752.5377 | TRUE | FALSE | TRUE | 33.2173
1.5463 | 323.7575 | 9.9145 | 10756.1808 | TRUE | FALSE | TRUE | 33.223
1.5524 | 323.8001 | 9.9158 | 10759.0144 | TRUE | FALSE | TRUE | 33.2273
1.5585 | 323.8306 | 9.9167 | 10761.0381 | TRUE | FALSE | TRUE | 33.2305
1.5647 | 323.8488 | 9.9173 | 10762.2516 | TRUE | FALSE | TRUE | 33.2323
1.5708 | 323.8549 | 9.9175 | 10762.6548 | TRUE | FALSE | TRUE | 33.233
1.5769 | 323.8488 | 9.9173 | 10762.2476 | TRUE | FALSE | TRUE | 33.2323
1.5831 | 323.8305 | 9.9167 | 10761.03 | TRUE | FALSE | TRUE | 33.2304
1.5892 | 323.7999 | 9.9158 | 10759.0022 | TRUE | FALSE | TRUE | 33.2273
1.5954 | 323.7572 | 9.9145 | 10756.1645 | TRUE | FALSE | TRUE | 33.2229
1.6015 | 323.7023 | 9.9128 | 10752.5174 | TRUE | FALSE | TRUE | 33.2173
1.6076 | 323.6353 | 9.9108 | 10748.0615 | TRUE | FALSE | TRUE | 33.2104
1.6138 | 323.556 | 9.9083 | 10742.7972 | TRUE | FALSE | TRUE | 33.2023
1.6199 | 323.4646 | 9.9055 | 10736.7256 | TRUE | FALSE | TRUE | 33.1929
1.626 | 323.3609 | 9.9024 | 10729.8474 | TRUE | FALSE | TRUE | 33.1823
1.6322 | 323.2451 | 9.8988 | 10722.1637 | TRUE | FALSE | TRUE | 33.1704
1.6383 | 323.1172 | 9.8949 | 10713.6757 | TRUE | FALSE | TRUE | 33.1572
1.6444 | 322.977 | 9.8906 | 10704.3847 | TRUE | FALSE | TRUE | 33.1429
1.6506 | 322.8247 | 9.8859 | 10694.292 | TRUE | FALSE | TRUE | 33.1272
1.6567 | 322.6603 | 9.8809 | 10683.3992 | TRUE | FALSE | TRUE | 33.1104
1.6629 | 322.4837 | 9.8755 | 10671.7079 | TRUE | FALSE | TRUE | 33.0922
1.669 | 322.2949 | 9.8697 | 10659.2199 | TRUE | FALSE | TRUE | 33.0729
1.6751 | 322.0941 | 9.8636 | 10645.937 | TRUE | FALSE | TRUE | 33.0523
1.6813 | 321.8811 | 9.857 | 10631.8613 | TRUE | FALSE | TRUE | 33.0304
1.6874 | 321.6559 | 9.8501 | 10616.9949 | TRUE | FALSE | TRUE | 33.0073
1.6935 | 321.4187 | 9.8429 | 10601.3399 | TRUE | FALSE | TRUE | 32.983
1.6997 | 321.1694 | 9.8352 | 10584.8989 | TRUE | FALSE | TRUE | 32.9574
1.7058 | 320.908 | 9.8272 | 10567.6742 | TRUE | FALSE | TRUE | 32.9305
1.7119 | 320.6344 | 9.8189 | 10549.6684 | TRUE | FALSE | TRUE | 32.9025
1.7181 | 320.3489 | 9.8101 | 10530.8842 | TRUE | FALSE | TRUE | 32.8732
1.7242 | 320.0512 | 9.801 | 10511.3246 | TRUE | FALSE | TRUE | 32.8426
1.7303 | 319.7415 | 9.7915 | 10490.9924 | TRUE | FALSE | TRUE | 32.8109
1.7365 | 319.4198 | 9.7817 | 10469.8907 | TRUE | FALSE | TRUE | 32.7778
1.7426 | 319.0861 | 9.7715 | 10448.0226 | TRUE | FALSE | TRUE | 32.7436
1.7488 | 318.7403 | 9.7609 | 10425.3915 | TRUE | FALSE | TRUE | 32.7081
1.7549 | 318.3825 | 9.7499 | 10402.0008 | TRUE | FALSE | TRUE | 32.6714
1.761 | 318.0128 | 9.7386 | 10377.8539 | TRUE | FALSE | TRUE | 32.6335
1.7672 | 317.631 | 9.7269 | 10352.9546 | TRUE | FALSE | TRUE | 32.5943
1.7733 | 317.2373 | 9.7148 | 10327.3065 | TRUE | FALSE | TRUE | 32.5539
1.7794 | 316.8317 | 9.7024 | 10300.9136 | TRUE | FALSE | TRUE | 32.5123
1.7856 | 316.4142 | 9.6896 | 10273.7798 | TRUE | FALSE | TRUE | 32.4694
1.7917 | 315.9847 | 9.6765 | 10245.9093 | TRUE | FALSE | TRUE | 32.4253
1.7978 | 315.5433 | 9.663 | 10217.3061 | TRUE | FALSE | TRUE | 32.38
1.804 | 315.0901 | 9.6491 | 10187.9746 | TRUE | FALSE | TRUE | 32.3335
1.8101 | 314.6249 | 9.6348 | 10157.9192 | TRUE | FALSE | TRUE | 32.2858
1.8163 | 314.148 | 9.6202 | 10127.1445 | TRUE | FALSE | TRUE | 32.2369
1.8224 | 313.6592 | 9.6053 | 10095.6551 | TRUE | FALSE | TRUE | 32.1867
1.8285 | 313.1586 | 9.5899 | 10063.4557 | TRUE | FALSE | TRUE | 32.1353
1.8347 | 312.6462 | 9.5742 | 10030.5511 | TRUE | FALSE | TRUE | 32.0828
1.8408 | 312.1221 | 9.5582 | 9996.9464 | TRUE | FALSE | TRUE | 32.029
1.8469 | 311.5861 | 9.5418 | 9962.6466 | TRUE | FALSE | TRUE | 31.974
1.8531 | 311.0385 | 9.525 | 9927.6569 | TRUE | FALSE | TRUE | 31.9178
1.8592 | 310.4792 | 9.5079 | 9891.9824 | TRUE | FALSE | TRUE | 31.8604
1.8653 | 309.9081 | 9.4904 | 9855.6287 | TRUE | FALSE | TRUE | 31.8018
1.8715 | 309.3254 | 9.4725 | 9818.6011 | TRUE | FALSE | TRUE | 31.742
1.8776 | 308.731 | 9.4543 | 9780.9053 | TRUE | FALSE | TRUE | 31.681
1.8837 | 308.1251 | 9.4358 | 9742.547 | TRUE | FALSE | TRUE | 31.6188
1.8899 | 307.5075 | 9.4169 | 9703.5318 | TRUE | FALSE | TRUE | 31.5554
1.896 | 306.8783 | 9.3976 | 9663.8657 | TRUE | FALSE | TRUE | 31.4909
1.9022 | 306.2376 | 9.378 | 9623.5546 | TRUE | FALSE | TRUE | 31.4251
1.9083 | 305.5854 | 9.358 | 9582.6047 | TRUE | FALSE | TRUE | 31.3582
1.9144 | 304.9216 | 9.3377 | 9541.0221 | TRUE | FALSE | TRUE | 31.2901
1.9206 | 304.2464 | 9.317 | 9498.813 | TRUE | FALSE | TRUE | 31.2208
1.9267 | 303.5597 | 9.296 | 9455.9839 | TRUE | FALSE | TRUE | 31.1503
1.9328 | 302.8616 | 9.2746 | 9412.5411 | TRUE | FALSE | TRUE | 31.0787
1.939 | 302.1521 | 9.2529 | 9368.4912 | TRUE | FALSE | TRUE | 31.0059
1.9451 | 301.4312 | 9.2308 | 9323.8408 | TRUE | FALSE | TRUE | 30.9319
1.9512 | 300.699 | 9.2084 | 9278.5967 | TRUE | FALSE | TRUE | 30.8568
1.9574 | 299.9554 | 9.1856 | 9232.7656 | TRUE | FALSE | TRUE | 30.7805
1.9635 | 299.2005 | 9.1625 | 9186.3546 | TRUE | FALSE | TRUE | 30.703
1.9697 | 298.4344 | 9.139 | 9139.3705 | TRUE | FALSE | TRUE | 30.6244
1.9758 | 297.6571 | 9.1152 | 9091.8204 | TRUE | FALSE | TRUE | 30.5446
1.9819 | 296.8685 | 9.0911 | 9043.7116 | TRUE | FALSE | TRUE | 30.4637
1.9881 | 296.0688 | 9.0666 | 8995.0512 | TRUE | FALSE | TRUE | 30.3816
1.9942 | 295.2579 | 9.0418 | 8945.8466 | TRUE | FALSE | TRUE | 30.2984
2.0003 | 294.4359 | 9.0166 | 8896.1051 | TRUE | FALSE | TRUE | 30.2141
2.0065 | 293.6028 | 8.9911 | 8845.8344 | TRUE | FALSE | TRUE | 30.1286
2.0126 | 292.7586 | 8.9652 | 8795.0419 | TRUE | FALSE | TRUE | 30.042
2.0187 | 291.9035 | 8.939 | 8743.7352 | TRUE | FALSE | TRUE | 29.9542
2.0249 | 291.0373 | 8.9125 | 8691.9223 | TRUE | FALSE | TRUE | 29.8653
2.031 | 290.1602 | 8.8856 | 8639.6107 | TRUE | FALSE | TRUE | 29.7753
2.0371 | 289.2722 | 8.8585 | 8586.8084 | TRUE | FALSE | TRUE | 29.6842
2.0433 | 288.3732 | 8.8309 | 8533.5234 | TRUE | FALSE | TRUE | 29.5919
2.0494 | 287.4635 | 8.8031 | 8479.7637 | TRUE | FALSE | TRUE | 29.4986
2.0556 | 286.5429 | 8.7749 | 8425.5374 | TRUE | FALSE | TRUE | 29.4041
2.0617 | 285.6115 | 8.7463 | 8370.8526 | TRUE | FALSE | TRUE | 29.3085
2.0678 | 284.6693 | 8.7175 | 8315.7175 | TRUE | FALSE | TRUE | 29.2119
2.074 | 283.7164 | 8.6883 | 8260.1406 | TRUE | FALSE | TRUE | 29.1141
2.0801 | 282.7529 | 8.6588 | 8204.1301 | TRUE | FALSE | TRUE | 29.0152
2.0862 | 281.7787 | 8.629 | 8147.6945 | TRUE | FALSE | TRUE | 28.9152
2.0924 | 280.7939 | 8.5988 | 8090.8423 | TRUE | FALSE | TRUE | 28.8142
2.0985 | 279.7985 | 8.5683 | 8033.5821 | TRUE | FALSE | TRUE | 28.712
2.1046 | 278.7926 | 8.5375 | 7975.9224 | TRUE | FALSE | TRUE | 28.6088
2.1108 | 277.7762 | 8.5064 | 7917.8719 | TRUE | FALSE | TRUE | 28.5045
2.1169 | 276.7493 | 8.475 | 7859.4395 | TRUE | FALSE | TRUE | 28.3991
2.1231 | 275.712 | 8.4432 | 7800.6339 | TRUE | FALSE | TRUE | 28.2927
2.1292 | 274.6644 | 8.4111 | 7741.4639 | TRUE | FALSE | TRUE | 28.1852
2.1353 | 273.6064 | 8.3787 | 7681.9385 | TRUE | FALSE | TRUE | 28.0766
2.1415 | 272.538 | 8.346 | 7622.0666 | TRUE | FALSE | TRUE | 27.967
2.1476 | 271.4595 | 8.313 | 7561.8572 | TRUE | FALSE | TRUE | 27.8563
2.1537 | 270.3707 | 8.2796 | 7501.3195 | TRUE | FALSE | TRUE | 27.7446
2.1599 | 269.2717 | 8.246 | 7440.4625 | TRUE | FALSE | TRUE | 27.6318
2.166 | 268.1626 | 8.212 | 7379.2954 | TRUE | FALSE | TRUE | 27.518
2.1721 | 267.0434 | 8.1777 | 7317.8274 | TRUE | FALSE | TRUE | 27.4031
2.1783 | 265.9141 | 8.1432 | 7256.0678 | TRUE | FALSE | TRUE | 27.2873
2.1844 | 264.7749 | 8.1083 | 7194.0258 | TRUE | FALSE | TRUE | 27.1703
2.1905 | 263.6256 | 8.0731 | 7131.7109 | TRUE | FALSE | TRUE | 27.0524
2.1967 | 262.4665 | 8.0376 | 7069.1323 | TRUE | FALSE | TRUE | 26.9335
2.2028 | 261.2974 | 8.0018 | 7006.2996 | TRUE | FALSE | TRUE | 26.8135
2.209 | 260.1185 | 7.9657 | 6943.2221 | TRUE | FALSE | TRUE | 26.6925
2.2151 | 258.9299 | 7.9293 | 6879.9094 | TRUE | FALSE | TRUE | 26.5706
2.2212 | 257.7314 | 7.8926 | 6816.3711 | TRUE | FALSE | TRUE | 26.4476
2.2274 | 256.5233 | 7.8556 | 6752.6166 | TRUE | FALSE | TRUE | 26.3236
2.2335 | 255.3055 | 7.8183 | 6688.6556 | TRUE | FALSE | TRUE | 26.1986
2.2396 | 254.0781 | 7.7807 | 6624.4977 | TRUE | FALSE | TRUE | 26.0727
2.2458 | 252.8411 | 7.7428 | 6560.1526 | TRUE | FALSE | TRUE | 25.9457
2.2519 | 251.5947 | 7.7046 | 6495.63 | TRUE | FALSE | TRUE | 25.8178
2.258 | 250.3387 | 7.6662 | 6430.9395 | TRUE | FALSE | TRUE | 25.689
2.2642 | 249.0733 | 7.6274 | 6366.091 | TRUE | FALSE | TRUE | 25.5591
2.2703 | 247.7985 | 7.5884 | 6301.0942 | TRUE | FALSE | TRUE | 25.4283
2.2764 | 246.5145 | 7.5491 | 6235.9589 | TRUE | FALSE | TRUE | 25.2965
2.2826 | 245.2211 | 7.5095 | 6170.6948 | TRUE | FALSE | TRUE | 25.1638
2.2887 | 243.9185 | 7.4696 | 6105.3119 | TRUE | FALSE | TRUE | 25.0301
2.2949 | 242.6067 | 7.4294 | 6039.8199 | TRUE | FALSE | TRUE | 24.8955
2.301 | 241.2858 | 7.389 | 5974.2288 | TRUE | FALSE | TRUE | 24.76
2.3071 | 239.9558 | 7.3482 | 5908.5484 | TRUE | FALSE | TRUE | 24.6235
2.3133 | 238.6167 | 7.3072 | 5842.7886 | TRUE | FALSE | TRUE | 24.4861
2.3194 | 237.2687 | 7.2659 | 5776.9593 | TRUE | FALSE | TRUE | 24.3478
2.3255 | 235.9117 | 7.2244 | 5711.0704 | TRUE | FALSE | TRUE | 24.2085
2.3317 | 234.5459 | 7.1826 | 5645.1319 | TRUE | FALSE | TRUE | 24.0683
2.3378 | 233.1712 | 7.1405 | 5579.1536 | TRUE | FALSE | TRUE | 23.9273
2.3439 | 231.7878 | 7.0981 | 5513.1455 | TRUE | FALSE | TRUE | 23.7853
2.3501 | 230.3956 | 7.0555 | 5447.1176 | TRUE | FALSE | TRUE | 23.6425
2.3562 | 228.9947 | 7.0126 | 3775.24 | FALSE | FALSE | FALSE | 16.4861
2.3624 | 227.5853 | 6.9694 | 3728.9094 | FALSE | FALSE | FALSE | 16.3847
2.3685 | 226.1672 | 6.926 | 3682.5859 | FALSE | FALSE | FALSE | 16.2826
2.3746 | 224.7407 | 6.8823 | 3636.2763 | FALSE | FALSE | FALSE | 16.1799
2.3808 | 223.3056 | 6.8383 | 3589.9876 | FALSE | FALSE | FALSE | 16.0766
2.3869 | 221.8622 | 6.7941 | 3543.7269 | FALSE | FALSE | FALSE | 15.9726
2.393 | 220.4104 | 6.7497 | 3497.5011 | FALSE | FALSE | FALSE | 15.8681
2.3992 | 218.9503 | 6.705 | 3451.3171 | FALSE | FALSE | FALSE | 15.763
2.4053 | 217.482 | 6.66 | 3405.182 | FALSE | FALSE | FALSE | 15.6573
2.4114 | 216.0055 | 6.6148 | 3359.1026 | FALSE | FALSE | FALSE | 15.551
2.4176 | 214.5209 | 6.5693 | 3313.0859 | FALSE | FALSE | FALSE | 15.4441
2.4237 | 213.0282 | 6.5236 | 3267.1388 | FALSE | FALSE | FALSE | 15.3367
2.4298 | 211.5274 | 6.4777 | 3221.2683 | FALSE | FALSE | FALSE | 15.2286
2.436 | 210.0187 | 6.4315 | 3175.4812 | FALSE | FALSE | FALSE | 15.12
2.4421 | 208.5021 | 6.385 | 3129.7845 | FALSE | FALSE | FALSE | 15.0108
2.4483 | 206.9776 | 6.3383 | 3084.185 | FALSE | FALSE | FALSE | 14.9011
2.4544 | 205.4454 | 6.2914 | 3038.6896 | FALSE | FALSE | FALSE | 14.7907
2.4605 | 203.9054 | 6.2442 | 2993.3051 | FALSE | FALSE | FALSE | 14.6799
2.4667 | 202.3577 | 6.1969 | 2948.0385 | FALSE | FALSE | FALSE | 14.5685
2.4728 | 200.8024 | 6.1492 | 2902.8964 | FALSE | FALSE | FALSE | 14.4565
2.4789 | 199.2396 | 6.1014 | 2857.8857 | FALSE | FALSE | FALSE | 14.344
2.4851 | 197.6692 | 6.0533 | 2813.0132 | FALSE | FALSE | FALSE | 14.2309
2.4912 | 196.0915 | 6.005 | 2768.2857 | FALSE | FALSE | FALSE | 14.1173
2.4973 | 194.5063 | 5.9564 | 2723.7098 | FALSE | FALSE | FALSE | 14.0032
2.5035 | 192.9138 | 5.9076 | 2679.2923 | FALSE | FALSE | FALSE | 13.8885
2.5096 | 191.314 | 5.8587 | 2635.0399 | FALSE | FALSE | FALSE | 13.7734
2.5158 | 189.7071 | 5.8094 | 2590.9593 | FALSE | FALSE | FALSE | 13.6577
2.5219 | 188.093 | 5.76 | 2547.057 | FALSE | FALSE | FALSE | 13.5415
2.528 | 186.4718 | 5.7104 | 2503.3397 | FALSE | FALSE | FALSE | 13.4248
2.5342 | 184.8436 | 5.6605 | 2459.8139 | FALSE | FALSE | FALSE | 13.3075
2.5403 | 183.2084 | 5.6104 | 2416.4863 | FALSE | FALSE | FALSE | 13.1898
2.5464 | 181.5663 | 5.5602 | 2373.3634 | FALSE | FALSE | FALSE | 13.0716
2.5526 | 179.9174 | 5.5097 | 2330.4516 | FALSE | FALSE | FALSE | 12.9529
2.5587 | 178.2618 | 5.459 | 2287.7574 | FALSE | FALSE | FALSE | 12.8337
2.5648 | 176.5994 | 5.408 | 2245.2872 | FALSE | FALSE | FALSE | 12.714
2.571 | 174.9303 | 5.3569 | 2203.0475 | FALSE | FALSE | FALSE | 12.5939
2.5771 | 173.2547 | 5.3056 | 2161.0446 | FALSE | FALSE | FALSE | 12.4732
2.5832 | 171.5726 | 5.2541 | 2119.2848 | FALSE | FALSE | FALSE | 12.3521
2.5894 | 169.884 | 5.2024 | 2077.7744 | FALSE | FALSE | FALSE | 12.2306
2.5955 | 168.189 | 5.1505 | 2036.5197 | FALSE | FALSE | FALSE | 12.1085
2.6017 | 166.4876 | 5.0984 | 1995.5268 | FALSE | FALSE | FALSE | 11.986
2.6078 | 164.78 | 5.0461 | 1954.802 | FALSE | FALSE | FALSE | 11.8631
2.6139 | 163.0662 | 4.9936 | 1914.3514 | FALSE | FALSE | FALSE | 11.7397
2.6201 | 161.3463 | 4.9409 | 1874.1811 | FALSE | FALSE | FALSE | 11.6159
2.6262 | 159.6203 | 4.8881 | 1834.2971 | FALSE | FALSE | FALSE | 11.4916
2.6323 | 157.8882 | 4.8351 | 1794.7054 | FALSE | FALSE | FALSE | 11.3669
2.6385 | 156.1503 | 4.7818 | 1755.412 | FALSE | FALSE | FALSE | 11.2418
2.6446 | 154.4064 | 4.7284 | 1716.4228 | FALSE | FALSE | FALSE | 11.1163
2.6507 | 152.6568 | 4.6748 | 1677.7437 | FALSE | FALSE | FALSE | 10.9903
2.6569 | 150.9013 | 4.6211 | 1639.3805 | FALSE | FALSE | FALSE | 10.8639
2.663 | 149.1402 | 4.5672 | 1601.339 | FALSE | FALSE | FALSE | 10.7371
2.6692 | 147.3735 | 4.5131 | 1563.625 | FALSE | FALSE | FALSE | 10.6099
2.6753 | 145.6013 | 4.4588 | 1526.244 | FALSE | FALSE | FALSE | 10.4824
2.6814 | 143.8235 | 4.4043 | 1489.2017 | FALSE | FALSE | FALSE | 10.3544
2.6876 | 142.0404 | 4.3497 | 1452.5037 | FALSE | FALSE | FALSE | 10.226
2.6937 | 140.2519 | 4.295 | 1416.1556 | FALSE | FALSE | FALSE | 10.0972
2.6998 | 138.4581 | 4.24 | 1380.1627 | FALSE | FALSE | FALSE | 9.9681
2.706 | 136.6591 | 4.1849 | 1344.5306 | FALSE | FALSE | FALSE | 9.8386
2.7121 | 134.855 | 4.1297 | 1309.2646 | FALSE | FALSE | FALSE | 9.7087
2.7182 | 133.0457 | 4.0743 | 1274.37 | FALSE | FALSE | FALSE | 9.5784
2.7244 | 131.2315 | 4.0187 | 1239.852 | FALSE | FALSE | FALSE | 9.4478
2.7305 | 129.4123 | 3.963 | 1205.7159 | FALSE | FALSE | FALSE | 9.3169
2.7366 | 127.5883 | 3.9072 | 1171.9668 | FALSE | FALSE | FALSE | 9.1855
2.7428 | 125.7595 | 3.8512 | 1138.6097 | FALSE | FALSE | FALSE | 9.0539
2.7489 | 123.9259 | 3.795 | 1105.6498 | FALSE | FALSE | FALSE | 8.9219
2.7551 | 122.0876 | 3.7387 | 1073.0919 | FALSE | FALSE | FALSE | 8.7895
2.7612 | 120.2448 | 3.6823 | 1040.941 | FALSE | FALSE | FALSE | 8.6568
2.7673 | 118.3974 | 3.6257 | 1009.2019 | FALSE | FALSE | FALSE | 8.5239
2.7735 | 116.5456 | 3.569 | 977.8793 | FALSE | FALSE | FALSE | 8.3905
2.7796 | 114.6894 | 3.5122 | 946.9781 | FALSE | FALSE | FALSE | 8.2569
2.7857 | 112.8288 | 3.4552 | 916.5029 | FALSE | FALSE | FALSE | 8.1229
2.7919 | 110.9641 | 3.3981 | 886.4582 | FALSE | FALSE | FALSE | 7.9887
2.798 | 109.0951 | 3.3408 | 856.8486 | FALSE | FALSE | FALSE | 7.8541
2.8041 | 107.222 | 3.2835 | 827.6785 | FALSE | FALSE | FALSE | 7.7193
2.8103 | 105.3449 | 3.226 | 798.9523 | FALSE | FALSE | FALSE | 7.5842
2.8164 | 103.4639 | 3.1684 | 770.6744 | FALSE | FALSE | FALSE | 7.4487
2.8226 | 101.5789 | 3.1107 | 742.849 | FALSE | FALSE | FALSE | 7.313
2.8287 | 99.6901 | 3.0528 | 715.4803 | FALSE | FALSE | FALSE | 7.177
2.8348 | 97.7976 | 2.9949 | 688.5724 | FALSE | FALSE | FALSE | 7.0408
2.841 | 95.9013 | 2.9368 | 662.1295 | FALSE | FALSE | FALSE | 6.9043
2.8471 | 94.0015 | 2.8786 | 636.1553 | FALSE | FALSE | FALSE | 6.7675
2.8532 | 92.0981 | 2.8203 | 610.6539 | FALSE | FALSE | FALSE | 6.6305
2.8594 | 90.1913 | 2.7619 | 585.6292 | FALSE | FALSE | FALSE | 6.4932
2.8655 | 88.281 | 2.7035 | 561.0848 | FALSE | FALSE | FALSE | 6.3557
2.8716 | 86.3675 | 2.6449 | 537.0245 | FALSE | FALSE | FALSE | 6.2179
2.8778 | 84.4507 | 2.5862 | 513.4519 | FALSE | FALSE | FALSE | 6.0799
2.8839 | 82.5307 | 2.5274 | 490.3705 | FALSE | FALSE | FALSE | 5.9417
2.89 | 80.6076 | 2.4685 | 467.7839 | FALSE | FALSE | FALSE | 5.8032
2.8962 | 78.6814 | 2.4095 | 445.6954 | FALSE | FALSE | FALSE | 5.6646
2.9023 | 76.7523 | 2.3504 | 424.1084 | FALSE | FALSE | FALSE | 5.5257
2.9085 | 74.8204 | 2.2912 | 403.026 | FALSE | FALSE | FALSE | 5.3866
2.9146 | 72.8855 | 2.232 | 382.4516 | FALSE | FALSE | FALSE | 5.2473
2.9207 | 70.948 | 2.1727 | 362.3881 | FALSE | FALSE | FALSE | 5.1078
2.9269 | 69.0078 | 2.1132 | 342.8386 | FALSE | FALSE | FALSE | 4.9681
2.933 | 67.065 | 2.0537 | 323.806 | FALSE | FALSE | FALSE | 4.8282
2.9391 | 65.1196 | 1.9942 | 305.2933 | FALSE | FALSE | FALSE | 4.6882
2.9453 | 63.1718 | 1.9345 | 287.3032 | FALSE | FALSE | FALSE | 4.548
2.9514 | 61.2216 | 1.8748 | 269.8383 | FALSE | FALSE | FALSE | 4.4076
2.9575 | 59.2692 | 1.815 | 252.9014 | FALSE | FALSE | FALSE | 4.267
2.9637 | 57.3145 | 1.7552 | 236.495 | FALSE | FALSE | FALSE | 4.1263
2.9698 | 55.3576 | 1.6952 | 220.6216 | FALSE | FALSE | FALSE | 3.9854
2.976 | 53.3986 | 1.6352 | 205.2835 | FALSE | FALSE | FALSE | 3.8444
2.9821 | 51.4377 | 1.5752 | 190.483 | FALSE | FALSE | FALSE | 3.7032
2.9882 | 49.4748 | 1.5151 | 176.2225 | FALSE | FALSE | FALSE | 3.5619
2.9944 | 47.51 | 1.4549 | 162.504 | FALSE | FALSE | FALSE | 3.4204
3.0005 | 45.5435 | 1.3947 | 149.3295 | FALSE | FALSE | FALSE | 3.2788
3.0066 | 43.5752 | 1.3344 | 136.7012 | FALSE | FALSE | FALSE | 3.1371
3.0128 | 41.6053 | 1.2741 | 124.6209 | FALSE | FALSE | FALSE | 2.9953
3.0189 | 39.6338 | 1.2137 | 113.0903 | FALSE | FALSE | FALSE | 2.8534
3.025 | 37.6609 | 1.1533 | 102.1113 | FALSE | FALSE | FALSE | 2.7113
3.0312 | 35.6865 | 1.0928 | 91.6855 | FALSE | FALSE | FALSE | 2.5692
3.0373 | 33.7107 | 1.0323 | 81.8145 | FALSE | FALSE | FALSE | 2.427
3.0434 | 31.7338 | 0.97179 | 72.4997 | FALSE | FALSE | FALSE | 2.2846
3.0496 | 29.7556 | 0.91121 | 63.7426 | FALSE | FALSE | FALSE | 2.1422
3.0557 | 27.7763 | 0.8506 | 55.5445 | FALSE | FALSE | FALSE | 1.9997
3.0619 | 25.7959 | 0.78995 | 47.9065 | FALSE | FALSE | FALSE | 1.8571
3.068 | 23.8146 | 0.72928 | 40.83 | FALSE | FALSE | FALSE | 1.7145
3.0741 | 21.8323 | 0.66858 | 34.3158 | FALSE | FALSE | FALSE | 1.5718
3.0803 | 19.8493 | 0.60785 | 28.3651 | FALSE | FALSE | FALSE | 1.429
3.0864 | 17.8655 | 0.5471 | 22.9786 | FALSE | FALSE | FALSE | 1.2862
3.0925 | 15.881 | 0.48633 | 18.1573 | FALSE | FALSE | FALSE | 1.1433
3.0987 | 13.896 | 0.42554 | 13.9018 | FALSE | FALSE | FALSE | 1.0004
3.1048 | 11.9104 | 0.36473 | 10.2128 | FALSE | FALSE | FALSE | 0.85747
3.1109 | 9.9244 | 0.30392 | 7.0908 | FALSE | FALSE | FALSE | 0.71449
3.1171 | 7.9379 | 0.24309 | 4.5364 | FALSE | FALSE | FALSE | 0.57148
3.1232 | 5.9512 | 0.18225 | 2.5498 | FALSE | FALSE | FALSE | 0.42845
3.1294 | 3.9643 | 0.1214 | 1.1314 | FALSE | FALSE | FALSE | 0.2854
3.1355 | 1.9772 | 0.060549 | 0.28145 | FALSE | FALSE | FALSE | 0.14235
3.1416 | -0.0099358 | -0.00030427 | 7.1073e-06 | FALSE | FALSE | FALSE | -0.00071532
3.1478 | -1.9971 | -0.061157 | 0.28714 | FALSE | FALSE | FALSE | -0.14378
3.1539 | -3.9842 | -0.12201 | 1.1428 | FALSE | FALSE | FALSE | -0.28683
3.16 | -5.9711 | -0.18285 | 2.5669 | FALSE | FALSE | FALSE | -0.42988
3.1662 | -7.9578 | -0.24369 | 4.5591 | FALSE | FALSE | FALSE | -0.57291
3.1723 | -9.9442 | -0.30452 | 7.1193 | FALSE | FALSE | FALSE | -0.71592
3.1784 | -11.9302 | -0.36534 | 10.2469 | FALSE | FALSE | FALSE | -0.8589
3.1846 | -13.9158 | -0.42615 | 13.9416 | FALSE | FALSE | FALSE | -1.0018
3.1907 | -15.9009 | -0.48694 | 18.2027 | FALSE | FALSE | FALSE | -1.1448
3.1968 | -17.8853 | -0.54771 | 23.0297 | FALSE | FALSE | FALSE | -1.2876
3.203 | -19.8691 | -0.60846 | 28.4218 | FALSE | FALSE | FALSE | -1.4304
3.2091 | -21.8522 | -0.66918 | 34.3782 | FALSE | FALSE | FALSE | -1.5732
3.2153 | -23.8344 | -0.72989 | 40.8979 | FALSE | FALSE | FALSE | -1.7159
3.2214 | -25.8157 | -0.79056 | 47.9801 | FALSE | FALSE | FALSE | -1.8586
3.2275 | -27.7961 | -0.85121 | 55.6237 | FALSE | FALSE | FALSE | -2.0011
3.2337 | -29.7754 | -0.91182 | 63.8274 | FALSE | FALSE | FALSE | -2.1436
3.2398 | -31.7535 | -0.9724 | 72.5901 | FALSE | FALSE | FALSE | -2.286
3.2459 | -33.7305 | -1.0329 | 81.9105 | FALSE | FALSE | FALSE | -2.4284
3.2521 | -35.7062 | -1.0934 | 91.7871 | FALSE | FALSE | FALSE | -2.5706
3.2582 | -37.6806 | -1.1539 | 102.2184 | FALSE | FALSE | FALSE | -2.7128
3.2643 | -39.6535 | -1.2143 | 113.2029 | FALSE | FALSE | FALSE | -2.8548
3.2705 | -41.625 | -1.2747 | 124.739 | FALSE | FALSE | FALSE | -2.9967
3.2766 | -43.5949 | -1.335 | 136.8248 | FALSE | FALSE | FALSE | -3.1386
3.2828 | -45.5631 | -1.3953 | 149.4586 | FALSE | FALSE | FALSE | -3.2803
3.2889 | -47.5297 | -1.4555 | 162.6385 | FALSE | FALSE | FALSE | -3.4218
3.295 | -49.4944 | -1.5157 | 176.3624 | FALSE | FALSE | FALSE | -3.5633
3.3012 | -51.4573 | -1.5758 | 190.6284 | FALSE | FALSE | FALSE | -3.7046
3.3073 | -53.4182 | -1.6358 | 205.4342 | FALSE | FALSE | FALSE | -3.8458
3.3134 | -55.3772 | -1.6958 | 220.7777 | FALSE | FALSE | FALSE | -3.9868
3.3196 | -57.334 | -1.7558 | 236.6564 | FALSE | FALSE | FALSE | -4.1277
3.3257 | -59.2887 | -1.8156 | 253.0682 | FALSE | FALSE | FALSE | -4.2684
3.3318 | -61.2412 | -1.8754 | 270.0104 | FALSE | FALSE | FALSE | -4.409
3.338 | -63.1913 | -1.9351 | 287.4805 | FALSE | FALSE | FALSE | -4.5494
3.3441 | -65.1391 | -1.9948 | 305.4758 | FALSE | FALSE | FALSE | -4.6896
3.3502 | -67.0844 | -2.0543 | 323.9938 | FALSE | FALSE | FALSE | -4.8296
3.3564 | -69.0272 | -2.1138 | 343.0315 | FALSE | FALSE | FALSE | -4.9695
3.3625 | -70.9674 | -2.1733 | 362.5862 | FALSE | FALSE | FALSE | -5.1092
3.3687 | -72.9049 | -2.2326 | 382.6548 | FALSE | FALSE | FALSE | -5.2487
3.3748 | -74.8397 | -2.2918 | 403.2343 | FALSE | FALSE | FALSE | -5.388
3.3809 | -76.7716 | -2.351 | 424.3217 | FALSE | FALSE | FALSE | -5.5271
3.3871 | -78.7007 | -2.4101 | 445.9138 | FALSE | FALSE | FALSE | -5.6659
3.3932 | -80.6268 | -2.4691 | 468.0073 | FALSE | FALSE | FALSE | -5.8046
3.3993 | -82.5499 | -2.5279 | 490.5989 | FALSE | FALSE | FALSE | -5.9431
3.4055 | -84.4699 | -2.5867 | 513.6852 | FALSE | FALSE | FALSE | -6.0813
3.4116 | -86.3866 | -2.6454 | 537.2627 | FALSE | FALSE | FALSE | -6.2193
3.4177 | -88.3002 | -2.704 | 561.3279 | FALSE | FALSE | FALSE | -6.357
3.4239 | -90.2104 | -2.7625 | 585.8771 | FALSE | FALSE | FALSE | -6.4946
3.43 | -92.1172 | -2.8209 | 610.9066 | FALSE | FALSE | FALSE | -6.6318
3.4362 | -94.0205 | -2.8792 | 636.4127 | FALSE | FALSE | FALSE | -6.7689
3.4423 | -95.9203 | -2.9374 | 662.3916 | FALSE | FALSE | FALSE | -6.9056
3.4484 | -97.8165 | -2.9955 | 688.8392 | FALSE | FALSE | FALSE | -7.0422
3.4546 | -99.709 | -3.0534 | 715.7517 | FALSE | FALSE | FALSE | -7.1784
3.4607 | -101.5978 | -3.1113 | 743.125 | FALSE | FALSE | FALSE | -7.3144
3.4668 | -103.4827 | -3.169 | 770.955 | FALSE | FALSE | FALSE | -7.4501
3.473 | -105.3637 | -3.2266 | 799.2374 | FALSE | FALSE | FALSE | -7.5855
3.4791 | -107.2408 | -3.2841 | 827.968 | FALSE | FALSE | FALSE | -7.7206
3.4852 | -109.1138 | -3.3414 | 857.1425 | FALSE | FALSE | FALSE | -7.8555
3.4914 | -110.9827 | -3.3987 | 886.7565 | FALSE | FALSE | FALSE | -7.99
3.4975 | -112.8475 | -3.4558 | 916.8055 | FALSE | FALSE | FALSE | -8.1243
3.5036 | -114.708 | -3.5127 | 947.2851 | FALSE | FALSE | FALSE | -8.2582
3.5098 | -116.5641 | -3.5696 | 978.1905 | FALSE | FALSE | FALSE | -8.3919
3.5159 | -118.4159 | -3.6263 | 1009.5172 | FALSE | FALSE | FALSE | -8.5252
3.5221 | -120.2632 | -3.6829 | 1041.2604 | FALSE | FALSE | FALSE | -8.6582
3.5282 | -122.106 | -3.7393 | 1073.4155 | FALSE | FALSE | FALSE | -8.7908
3.5343 | -123.9442 | -3.7956 | 1105.9774 | FALSE | FALSE | FALSE | -8.9232
3.5405 | -125.7778 | -3.8517 | 1138.9413 | FALSE | FALSE | FALSE | -9.0552
3.5466 | -127.6066 | -3.9077 | 1172.3023 | FALSE | FALSE | FALSE | -9.1868
3.5527 | -129.4306 | -3.9636 | 1206.0553 | FALSE | FALSE | FALSE | -9.3182
3.5589 | -131.2497 | -4.0193 | 1240.1953 | FALSE | FALSE | FALSE | -9.4491
3.565 | -133.0639 | -4.0748 | 1274.7171 | FALSE | FALSE | FALSE | -9.5797
3.5711 | -134.873 | -4.1302 | 1309.6154 | FALSE | FALSE | FALSE | -9.71
3.5773 | -136.6771 | -4.1855 | 1344.8851 | FALSE | FALSE | FALSE | -9.8399
3.5834 | -138.4761 | -4.2406 | 1380.5209 | FALSE | FALSE | FALSE | -9.9694
3.5896 | -140.2698 | -4.2955 | 1416.5173 | FALSE | FALSE | FALSE | -10.0985
3.5957 | -142.0582 | -4.3503 | 1452.869 | FALSE | FALSE | FALSE | -10.2273
3.6018 | -143.8413 | -4.4049 | 1489.5704 | FALSE | FALSE | FALSE | -10.3556
3.608 | -145.619 | -4.4593 | 1526.6161 | FALSE | FALSE | FALSE | -10.4836
3.6141 | -147.3912 | -4.5136 | 1564.0005 | FALSE | FALSE | FALSE | -10.6112
3.6202 | -149.1579 | -4.5677 | 1601.7178 | FALSE | FALSE | FALSE | -10.7384
3.6264 | -150.9189 | -4.6216 | 1639.7626 | FALSE | FALSE | FALSE | -10.8652
3.6325 | -152.6743 | -4.6754 | 1678.129 | FALSE | FALSE | FALSE | -10.9916
3.6386 | -154.4239 | -4.729 | 1716.8112 | FALSE | FALSE | FALSE | -11.1175
3.6448 | -156.1677 | -4.7824 | 1755.8035 | FALSE | FALSE | FALSE | -11.2431
3.6509 | -157.9056 | -4.8356 | 1795.0999 | FALSE | FALSE | FALSE | -11.3682
3.657 | -159.6376 | -4.8886 | 1834.6945 | FALSE | FALSE | FALSE | -11.4929
3.6632 | -161.3635 | -4.9415 | 1874.5814 | FALSE | FALSE | FALSE | -11.6171
3.6693 | -163.0834 | -4.9941 | 1914.7546 | FALSE | FALSE | FALSE | -11.741
3.6755 | -164.7971 | -5.0466 | 1955.208 | FALSE | FALSE | FALSE | -11.8643
3.6816 | -166.5047 | -5.0989 | 1995.9355 | FALSE | FALSE | FALSE | -11.9873
3.6877 | -168.206 | -5.151 | 2036.931 | FALSE | FALSE | FALSE | -12.1097
3.6939 | -169.9009 | -5.2029 | 2078.1883 | FALSE | FALSE | FALSE | -12.2318
3.7 | -171.5894 | -5.2546 | 2119.7012 | FALSE | FALSE | FALSE | -12.3533
3.7061 | -173.2715 | -5.3061 | 2161.4634 | FALSE | FALSE | FALSE | -12.4744
3.7123 | -174.9471 | -5.3574 | 2203.4687 | FALSE | FALSE | FALSE | -12.5951
3.7184 | -176.616 | -5.4086 | 2245.7108 | FALSE | FALSE | FALSE | -12.7152
3.7245 | -178.2783 | -5.4595 | 2288.1832 | FALSE | FALSE | FALSE | -12.8349
3.7307 | -179.934 | -5.5102 | 2330.8796 | FALSE | FALSE | FALSE | -12.9541
3.7368 | -181.5828 | -5.5607 | 2373.7936 | FALSE | FALSE | FALSE | -13.0728
3.7429 | -183.2248 | -5.6109 | 2416.9186 | FALSE | FALSE | FALSE | -13.191
3.7491 | -184.8599 | -5.661 | 2460.2482 | FALSE | FALSE | FALSE | -13.3087
3.7552 | -186.488 | -5.7109 | 2503.7759 | FALSE | FALSE | FALSE | -13.4259
3.7614 | -188.1091 | -5.7605 | 2547.4951 | FALSE | FALSE | FALSE | -13.5426
3.7675 | -189.7232 | -5.8099 | 2591.3992 | FALSE | FALSE | FALSE | -13.6588
3.7736 | -191.3301 | -5.8591 | 2635.4816 | FALSE | FALSE | FALSE | -13.7745
3.7798 | -192.9297 | -5.9081 | 2679.7357 | FALSE | FALSE | FALSE | -13.8897
3.7859 | -194.5222 | -5.9569 | 2724.1548 | FALSE | FALSE | FALSE | -14.0043
3.792 | -196.1073 | -6.0054 | 2768.7322 | FALSE | FALSE | FALSE | -14.1185
3.7982 | -197.685 | -6.0538 | 2813.4613 | FALSE | FALSE | FALSE | -14.232
3.8043 | -199.2553 | -6.1018 | 2858.3352 | FALSE | FALSE | FALSE | -14.3451
3.8104 | -200.818 | -6.1497 | 2903.3472 | FALSE | FALSE | FALSE | -14.4576
3.8166 | -202.3732 | -6.1973 | 2948.4905 | FALSE | FALSE | FALSE | -14.5696
3.8227 | -203.9208 | -6.2447 | 2993.7584 | FALSE | FALSE | FALSE | -14.681
3.8289 | -205.4607 | -6.2919 | 3039.144 | FALSE | FALSE | FALSE | -14.7918
3.835 | -206.9929 | -6.3388 | 3084.6405 | FALSE | FALSE | FALSE | -14.9022
3.8411 | -208.5173 | -6.3855 | 3130.241 | FALSE | FALSE | FALSE | -15.0119
3.8473 | -210.0338 | -6.4319 | 3175.9386 | FALSE | FALSE | FALSE | -15.1211
3.8534 | -211.5425 | -6.4781 | 3221.7266 | FALSE | FALSE | FALSE | -15.2297
3.8595 | -213.0431 | -6.5241 | 3267.5979 | FALSE | FALSE | FALSE | -15.3377
3.8657 | -214.5358 | -6.5698 | 3313.5457 | FALSE | FALSE | FALSE | -15.4452
3.8718 | -216.0203 | -6.6152 | 3359.5631 | FALSE | FALSE | FALSE | -15.5521
3.8779 | -217.4967 | -6.6605 | 3405.6431 | FALSE | FALSE | FALSE | -15.6584
3.8841 | -218.965 | -6.7054 | 3451.7788 | FALSE | FALSE | FALSE | -15.7641
3.8902 | -220.425 | -6.7501 | 3497.9632 | FALSE | FALSE | FALSE | -15.8692
3.8963 | -221.8767 | -6.7946 | 3544.1894 | FALSE | FALSE | FALSE | -15.9737
3.9025 | -223.32 | -6.8388 | 3590.4504 | FALSE | FALSE | FALSE | -16.0776
3.9086 | -224.755 | -6.8827 | 3636.7393 | FALSE | FALSE | FALSE | -16.1809
3.9148 | -226.1814 | -6.9264 | 3683.049 | FALSE | FALSE | FALSE | -16.2836
3.9209 | -227.5994 | -6.9698 | 3729.3727 | FALSE | FALSE | FALSE | -16.3857
3.927 | -229.0088 | -7.013 | 5381.7402 | FALSE | TRUE | TRUE | -23.5001
3.9332 | -230.4095 | -7.0559 | 5447.7779 | FALSE | TRUE | TRUE | -23.6439
3.9393 | -231.8016 | -7.0985 | 5513.8057 | FALSE | TRUE | TRUE | -23.7867
3.9454 | -233.185 | -7.1409 | 5579.8135 | FALSE | TRUE | TRUE | -23.9287
3.9516 | -234.5596 | -7.183 | 5645.7915 | FALSE | TRUE | TRUE | -24.0698
3.9577 | -235.9253 | -7.2248 | 5711.7296 | FALSE | TRUE | TRUE | -24.2099
3.9638 | -237.2822 | -7.2664 | 5777.6179 | FALSE | TRUE | TRUE | -24.3491
3.97 | -238.6301 | -7.3076 | 5843.4466 | FALSE | TRUE | TRUE | -24.4875
3.9761 | -239.9691 | -7.3486 | 5909.2056 | FALSE | TRUE | TRUE | -24.6249
3.9823 | -241.299 | -7.3894 | 5974.8852 | FALSE | TRUE | TRUE | -24.7613
3.9884 | -242.6199 | -7.4298 | 6040.4754 | FALSE | TRUE | TRUE | -24.8969
3.9945 | -243.9315 | -7.47 | 6105.9663 | FALSE | TRUE | TRUE | -25.0315
4.0007 | -245.2341 | -7.5099 | 6171.3481 | FALSE | TRUE | TRUE | -25.1651
4.0068 | -246.5273 | -7.5495 | 6236.6109 | FALSE | TRUE | TRUE | -25.2978
4.0129 | -247.8113 | -7.5888 | 6301.7449 | FALSE | TRUE | TRUE | -25.4296
4.0191 | -249.086 | -7.6278 | 6366.7403 | FALSE | TRUE | TRUE | -25.5604
4.0252 | -250.3513 | -7.6666 | 6431.5872 | FALSE | TRUE | TRUE | -25.6902
4.0313 | -251.6072 | -7.705 | 6496.2761 | FALSE | TRUE | TRUE | -25.8191
4.0375 | -252.8536 | -7.7432 | 6560.797 | FALSE | TRUE | TRUE | -25.947
4.0436 | -254.0904 | -7.7811 | 6625.1402 | FALSE | TRUE | TRUE | -26.0739
4.0497 | -255.3177 | -7.8187 | 6689.2962 | FALSE | TRUE | TRUE | -26.1999
4.0559 | -256.5354 | -7.8559 | 6753.2552 | FALSE | TRUE | TRUE | -26.3248
4.062 | -257.7435 | -7.8929 | 6817.0075 | FALSE | TRUE | TRUE | -26.4488
4.0682 | -258.9418 | -7.9296 | 6880.5437 | FALSE | TRUE | TRUE | -26.5718
4.0743 | -260.1304 | -7.966 | 6943.8541 | FALSE | TRUE | TRUE | -26.6937
4.0804 | -261.3092 | -8.0021 | 7006.9291 | FALSE | TRUE | TRUE | -26.8147
4.0866 | -262.4781 | -8.0379 | 7069.7594 | FALSE | TRUE | TRUE | -26.9347
4.0927 | -263.6372 | -8.0734 | 7132.3354 | FALSE | TRUE | TRUE | -27.0536
4.0988 | -264.7863 | -8.1086 | 7194.6476 | FALSE | TRUE | TRUE | -27.1715
4.105 | -265.9255 | -8.1435 | 7256.6868 | FALSE | TRUE | TRUE | -27.2884
4.1111 | -267.0546 | -8.1781 | 7318.4436 | FALSE | TRUE | TRUE | -27.4043
4.1172 | -268.1738 | -8.2124 | 7379.9086 | FALSE | TRUE | TRUE | -27.5191
4.1234 | -269.2828 | -8.2463 | 7441.0726 | FALSE | TRUE | TRUE | -27.6329
4.1295 | -270.3816 | -8.28 | 7501.9265 | FALSE | TRUE | TRUE | -27.7457
4.1357 | -271.4703 | -8.3133 | 7562.461 | FALSE | TRUE | TRUE | -27.8574
4.1418 | -272.5488 | -8.3463 | 7622.667 | FALSE | TRUE | TRUE | -27.9681
4.1479 | -273.617 | -8.379 | 7682.5355 | FALSE | TRUE | TRUE | -28.0777
4.1541 | -274.6749 | -8.4114 | 7742.0574 | FALSE | TRUE | TRUE | -28.1863
4.1602 | -275.7225 | -8.4435 | 7801.2237 | FALSE | TRUE | TRUE | -28.2938
4.1663 | -276.7596 | -8.4753 | 7860.0257 | FALSE | TRUE | TRUE | -28.4002
4.1725 | -277.7864 | -8.5067 | 7918.4543 | FALSE | TRUE | TRUE | -28.5056
4.1786 | -278.8027 | -8.5378 | 7976.5009 | FALSE | TRUE | TRUE | -28.6098
4.1847 | -279.8085 | -8.5686 | 8034.1566 | FALSE | TRUE | TRUE | -28.7131
4.1909 | -280.8038 | -8.5991 | 8091.4129 | FALSE | TRUE | TRUE | -28.8152
4.197 | -281.7885 | -8.6293 | 8148.261 | FALSE | TRUE | TRUE | -28.9162
4.2031 | -282.7626 | -8.6591 | 8204.6923 | FALSE | TRUE | TRUE | -29.0162
4.2093 | -283.726 | -8.6886 | 8260.6985 | FALSE | TRUE | TRUE | -29.1151
4.2154 | -284.6788 | -8.7178 | 8316.2711 | FALSE | TRUE | TRUE | -29.2128
4.2216 | -285.6208 | -8.7466 | 8371.4017 | FALSE | TRUE | TRUE | -29.3095
4.2277 | -286.5521 | -8.7752 | 8426.0819 | FALSE | TRUE | TRUE | -29.4051
4.2338 | -287.4726 | -8.8033 | 8480.3036 | FALSE | TRUE | TRUE | -29.4995
4.24 | -288.3823 | -8.8312 | 8534.0586 | FALSE | TRUE | TRUE | -29.5929
4.2461 | -289.2811 | -8.8587 | 8587.3389 | FALSE | TRUE | TRUE | -29.6851
4.2522 | -290.169 | -8.8859 | 8640.1362 | FALSE | TRUE | TRUE | -29.7762
4.2584 | -291.046 | -8.9128 | 8692.4429 | FALSE | TRUE | TRUE | -29.8662
4.2645 | -291.9121 | -8.9393 | 8744.2508 | FALSE | TRUE | TRUE | -29.9551
4.2706 | -292.7671 | -8.9655 | 8795.5523 | FALSE | TRUE | TRUE | -30.0428
4.2768 | -293.6112 | -8.9913 | 8846.3397 | FALSE | TRUE | TRUE | -30.1294
4.2829 | -294.4442 | -9.0168 | 8896.6052 | FALSE | TRUE | TRUE | -30.2149
4.2891 | -295.266 | -9.042 | 8946.3413 | FALSE | TRUE | TRUE | -30.2993
4.2952 | -296.0768 | -9.0668 | 8995.5405 | FALSE | TRUE | TRUE | -30.3825
4.3013 | -296.8764 | -9.0913 | 9044.1954 | FALSE | TRUE | TRUE | -30.4645
4.3075 | -297.6649 | -9.1155 | 9092.2987 | FALSE | TRUE | TRUE | -30.5454
4.3136 | -298.4421 | -9.1393 | 9139.8431 | FALSE | TRUE | TRUE | -30.6252
4.3197 | -299.2081 | -9.1627 | 9186.8215 | FALSE | TRUE | TRUE | -30.7038
4.3259 | -299.9629 | -9.1858 | 9233.2268 | FALSE | TRUE | TRUE | -30.7812
4.332 | -300.7063 | -9.2086 | 9279.052 | FALSE | TRUE | TRUE | -30.8575
4.3381 | -301.4385 | -9.231 | 9324.2902 | FALSE | TRUE | TRUE | -30.9326
4.3443 | -302.1592 | -9.2531 | 9368.9346 | FALSE | TRUE | TRUE | -31.0066
4.3504 | -302.8686 | -9.2748 | 9412.9785 | FALSE | TRUE | TRUE | -31.0794
4.3565 | -303.5666 | -9.2962 | 9456.4152 | FALSE | TRUE | TRUE | -31.151
4.3627 | -304.2532 | -9.3172 | 9499.2382 | FALSE | TRUE | TRUE | -31.2215
4.3688 | -304.9283 | -9.3379 | 9541.441 | FALSE | TRUE | TRUE | -31.2908
4.375 | -305.592 | -9.3582 | 9583.0174 | FALSE | TRUE | TRUE | -31.3589
4.3811 | -306.2441 | -9.3782 | 9623.9609 | FALSE | TRUE | TRUE | -31.4258
4.3872 | -306.8847 | -9.3978 | 9664.2656 | FALSE | TRUE | TRUE | -31.4915
4.3934 | -307.5137 | -9.4171 | 9703.9252 | FALSE | TRUE | TRUE | -31.5561
4.3995 | -308.1312 | -9.436 | 9742.9338 | FALSE | TRUE | TRUE | -31.6194
4.4056 | -308.737 | -9.4545 | 9781.2856 | FALSE | TRUE | TRUE | -31.6816
4.4118 | -309.3313 | -9.4727 | 9818.9747 | FALSE | TRUE | TRUE | -31.7426
4.4179 | -309.9139 | -9.4906 | 9855.9956 | FALSE | TRUE | TRUE | -31.8024
4.424 | -310.4848 | -9.5081 | 9892.3425 | FALSE | TRUE | TRUE | -31.861
4.4302 | -311.044 | -9.5252 | 9928.0102 | FALSE | TRUE | TRUE | -31.9183
4.4363 | -311.5916 | -9.5419 | 9962.993 | FALSE | TRUE | TRUE | -31.9745
4.4425 | -312.1274 | -9.5584 | 9997.2859 | FALSE | TRUE | TRUE | -32.0295
4.4486 | -312.6514 | -9.5744 | 10030.8836 | FALSE | TRUE | TRUE | -32.0833
4.4547 | -313.1637 | -9.5901 | 10063.7811 | FALSE | TRUE | TRUE | -32.1359
4.4609 | -313.6641 | -9.6054 | 10095.9735 | FALSE | TRUE | TRUE | -32.1872
4.467 | -314.1528 | -9.6204 | 10127.4558 | FALSE | TRUE | TRUE | -32.2374
4.4731 | -314.6297 | -9.635 | 10158.2233 | FALSE | TRUE | TRUE | -32.2863
4.4793 | -315.0946 | -9.6492 | 10188.2715 | FALSE | TRUE | TRUE | -32.334
4.4854 | -315.5478 | -9.6631 | 10217.5957 | FALSE | TRUE | TRUE | -32.3805
4.4915 | -315.989 | -9.6766 | 10246.1916 | FALSE | TRUE | TRUE | -32.4258
4.4977 | -316.4184 | -9.6898 | 10274.0548 | FALSE | TRUE | TRUE | -32.4698
4.5038 | -316.8358 | -9.7025 | 10301.1812 | FALSE | TRUE | TRUE | -32.5127
4.5099 | -317.2413 | -9.715 | 10327.5667 | FALSE | TRUE | TRUE | -32.5543
4.5161 | -317.6349 | -9.727 | 10353.2073 | FALSE | TRUE | TRUE | -32.5947
4.5222 | -318.0165 | -9.7387 | 10378.0991 | FALSE | TRUE | TRUE | -32.6338
4.5284 | -318.3862 | -9.75 | 10402.2384 | FALSE | TRUE | TRUE | -32.6718
4.5345 | -318.7438 | -9.761 | 10425.6216 | FALSE | TRUE | TRUE | -32.7085
4.5406 | -319.0895 | -9.7716 | 10448.2451 | FALSE | TRUE | TRUE | -32.7439
4.5468 | -319.4231 | -9.7818 | 10470.1055 | FALSE | TRUE | TRUE | -32.7782
4.5529 | -319.7447 | -9.7916 | 10491.1995 | FALSE | TRUE | TRUE | -32.8112
4.559 | -320.0543 | -9.8011 | 10511.524 | FALSE | TRUE | TRUE | -32.8429
4.5652 | -320.3518 | -9.8102 | 10531.0759 | FALSE | TRUE | TRUE | -32.8735
4.5713 | -320.6372 | -9.819 | 10549.8523 | FALSE | TRUE | TRUE | -32.9028
4.5774 | -320.9106 | -9.8273 | 10567.8503 | FALSE | TRUE | TRUE | -32.9308
4.5836 | -321.1719 | -9.8353 | 10585.0672 | FALSE | TRUE | TRUE | -32.9576
4.5897 | -321.4211 | -9.843 | 10601.5004 | FALSE | TRUE | TRUE | -32.9832
4.5959 | -321.6583 | -9.8502 | 10617.1474 | FALSE | TRUE | TRUE | -33.0075
4.602 | -321.8833 | -9.8571 | 10632.006 | FALSE | TRUE | TRUE | -33.0306
4.6081 | -322.0961 | -9.8636 | 10646.0738 | FALSE | TRUE | TRUE | -33.0525
4.6143 | -322.2969 | -9.8698 | 10659.3487 | FALSE | TRUE | TRUE | -33.0731
4.6204 | -322.4855 | -9.8756 | 10671.8288 | FALSE | TRUE | TRUE | -33.0924
4.6265 | -322.662 | -9.881 | 10683.5121 | FALSE | TRUE | TRUE | -33.1105
4.6327 | -322.8263 | -9.886 | 10694.3969 | FALSE | TRUE | TRUE | -33.1274
4.6388 | -322.9785 | -9.8906 | 10704.4816 | FALSE | TRUE | TRUE | -33.143
4.6449 | -323.1185 | -9.8949 | 10713.7646 | FALSE | TRUE | TRUE | -33.1574
4.6511 | -323.2463 | -9.8989 | 10722.2446 | FALSE | TRUE | TRUE | -33.1705
4.6572 | -323.362 | -9.9024 | 10729.9202 | FALSE | TRUE | TRUE | -33.1824
4.6633 | -323.4655 | -9.9056 | 10736.7903 | FALSE | TRUE | TRUE | -33.193
4.6695 | -323.5569 | -9.9084 | 10742.8539 | FALSE | TRUE | TRUE | -33.2024
4.6756 | -323.636 | -9.9108 | 10748.11 | FALSE | TRUE | TRUE | -33.2105
4.6818 | -323.703 | -9.9128 | 10752.5579 | FALSE | TRUE | TRUE | -33.2174
4.6879 | -323.7577 | -9.9145 | 10756.1969 | FALSE | TRUE | TRUE | -33.223
4.694 | -323.8003 | -9.9158 | 10759.0265 | FALSE | TRUE | TRUE | -33.2274
4.7002 | -323.8307 | -9.9167 | 10761.0462 | FALSE | TRUE | TRUE | -33.2305
4.7063 | -323.8489 | -9.9173 | 10762.2557 | FALSE | TRUE | TRUE | -33.2323
4.7124 | -323.8549 | -9.9175 | 10762.6548 | FALSE | TRUE | TRUE | -33.233
4.7186 | -323.8487 | -9.9173 | 10762.2435 | FALSE | TRUE | TRUE | -33.2323
4.7247 | -323.8303 | -9.9167 | 10761.0219 | FALSE | TRUE | TRUE | -33.2304
4.7308 | -323.7998 | -9.9158 | 10758.99 | FALSE | TRUE | TRUE | -33.2273
4.737 | -323.757 | -9.9145 | 10756.1483 | FALSE | TRUE | TRUE | -33.2229
4.7431 | -323.702 | -9.9128 | 10752.4972 | FALSE | TRUE | TRUE | -33.2173
4.7493 | -323.6349 | -9.9108 | 10748.0371 | FALSE | TRUE | TRUE | -33.2104
4.7554 | -323.5556 | -9.9083 | 10742.7689 | FALSE | TRUE | TRUE | -33.2022
4.7615 | -323.4641 | -9.9055 | 10736.6932 | FALSE | TRUE | TRUE | -33.1928
4.7677 | -323.3604 | -9.9023 | 10729.811 | FALSE | TRUE | TRUE | -33.1822
4.7738 | -323.2445 | -9.8988 | 10722.1233 | FALSE | TRUE | TRUE | -33.1703
4.7799 | -323.1165 | -9.8949 | 10713.6313 | FALSE | TRUE | TRUE | -33.1572
4.7861 | -322.9763 | -9.8906 | 10704.3362 | FALSE | TRUE | TRUE | -33.1428
4.7922 | -322.8239 | -9.8859 | 10694.2396 | FALSE | TRUE | TRUE | -33.1272
4.7983 | -322.6594 | -9.8809 | 10683.3428 | FALSE | TRUE | TRUE | -33.1103
4.8045 | -322.4828 | -9.8755 | 10671.6475 | FALSE | TRUE | TRUE | -33.0921
4.8106 | -322.294 | -9.8697 | 10659.1555 | FALSE | TRUE | TRUE | -33.0728
4.8167 | -322.093 | -9.8635 | 10645.8686 | FALSE | TRUE | TRUE | -33.0522
4.8229 | -321.88 | -9.857 | 10631.7889 | FALSE | TRUE | TRUE | -33.0303
4.829 | -321.6548 | -9.8501 | 10616.9185 | FALSE | TRUE | TRUE | -33.0072
4.8352 | -321.4175 | -9.8428 | 10601.2597 | FALSE | TRUE | TRUE | -32.9828
4.8413 | -321.1681 | -9.8352 | 10584.8147 | FALSE | TRUE | TRUE | -32.9572
4.8474 | -320.9066 | -9.8272 | 10567.5861 | FALSE | TRUE | TRUE | -32.9304
4.8536 | -320.633 | -9.8188 | 10549.5764 | FALSE | TRUE | TRUE | -32.9023
4.8597 | -320.3474 | -9.8101 | 10530.7884 | FALSE | TRUE | TRUE | -32.873
4.8658 | -320.0497 | -9.801 | 10511.2249 | FALSE | TRUE | TRUE | -32.8425
4.872 | -319.74 | -9.7915 | 10490.8888 | FALSE | TRUE | TRUE | -32.8107
4.8781 | -319.4182 | -9.7816 | 10469.7832 | FALSE | TRUE | TRUE | -32.7777
4.8842 | -319.0844 | -9.7714 | 10447.9113 | FALSE | TRUE | TRUE | -32.7434
4.8904 | -318.7385 | -9.7608 | 10425.2764 | FALSE | TRUE | TRUE | -32.7079
4.8965 | -318.3807 | -9.7499 | 10401.8819 | FALSE | TRUE | TRUE | -32.6712
4.9027 | -318.0109 | -9.7385 | 10377.7313 | FALSE | TRUE | TRUE | -32.6333
4.9088 | -317.6291 | -9.7268 | 10352.8282 | FALSE | TRUE | TRUE | -32.5941
4.9149 | -317.2353 | -9.7148 | 10327.1764 | FALSE | TRUE | TRUE | -32.5537
4.9211 | -316.8297 | -9.7024 | 10300.7798 | FALSE | TRUE | TRUE | -32.512
4.9272 | -316.412 | -9.6896 | 10273.6423 | FALSE | TRUE | TRUE | -32.4692
4.9333 | -315.9825 | -9.6764 | 10245.7681 | FALSE | TRUE | TRUE | -32.4251
4.9395 | -315.5411 | -9.6629 | 10217.1612 | FALSE | TRUE | TRUE | -32.3798
4.9456 | -315.0878 | -9.649 | 10187.8261 | FALSE | TRUE | TRUE | -32.3333
4.9517 | -314.6226 | -9.6348 | 10157.7671 | FALSE | TRUE | TRUE | -32.2856
4.9579 | -314.1456 | -9.6202 | 10126.9888 | FALSE | TRUE | TRUE | -32.2366
4.964 | -313.6567 | -9.6052 | 10095.4958 | FALSE | TRUE | TRUE | -32.1864
4.9701 | -313.1561 | -9.5899 | 10063.2929 | FALSE | TRUE | TRUE | -32.1351
4.9763 | -312.6436 | -9.5742 | 10030.3848 | FALSE | TRUE | TRUE | -32.0825
4.9824 | -312.1194 | -9.5581 | 9996.7766 | FALSE | TRUE | TRUE | -32.0287
4.9886 | -311.5834 | -9.5417 | 9962.4734 | FALSE | TRUE | TRUE | -31.9737
4.9947 | -311.0357 | -9.5249 | 9927.4802 | FALSE | TRUE | TRUE | -31.9175
5.0008 | -310.4763 | -9.5078 | 9891.8023 | FALSE | TRUE | TRUE | -31.8601
5.007 | -309.9052 | -9.4903 | 9855.4452 | FALSE | TRUE | TRUE | -31.8015
5.0131 | -309.3225 | -9.4725 | 9818.4143 | FALSE | TRUE | TRUE | -31.7417
5.0192 | -308.728 | -9.4543 | 9780.7152 | FALSE | TRUE | TRUE | -31.6807
5.0254 | -308.122 | -9.4357 | 9742.3535 | FALSE | TRUE | TRUE | -31.6185
5.0315 | -307.5044 | -9.4168 | 9703.3351 | FALSE | TRUE | TRUE | -31.5551
5.0376 | -306.8752 | -9.3975 | 9663.6657 | FALSE | TRUE | TRUE | -31.4905
5.0438 | -306.2344 | -9.3779 | 9623.3515 | FALSE | TRUE | TRUE | -31.4248
5.0499 | -305.5821 | -9.3579 | 9582.3984 | FALSE | TRUE | TRUE | -31.3579
5.0561 | -304.9183 | -9.3376 | 9540.8126 | FALSE | TRUE | TRUE | -31.2897
5.0622 | -304.243 | -9.3169 | 9498.6004 | FALSE | TRUE | TRUE | -31.2204
5.0683 | -303.5563 | -9.2959 | 9455.7682 | FALSE | TRUE | TRUE | -31.15
5.0745 | -302.8581 | -9.2745 | 9412.3223 | FALSE | TRUE | TRUE | -31.0783
5.0806 | -302.1485 | -9.2528 | 9368.2694 | FALSE | TRUE | TRUE | -31.0055
5.0867 | -301.4276 | -9.2307 | 9323.616 | FALSE | TRUE | TRUE | -30.9315
5.0929 | -300.6953 | -9.2083 | 9278.369 | FALSE | TRUE | TRUE | -30.8564
5.099 | -299.9517 | -9.1855 | 9232.535 | FALSE | TRUE | TRUE | -30.7801
5.1051 | -299.1967 | -9.1624 | 9186.1211 | FALSE | TRUE | TRUE | -30.7026
5.1113 | -298.4306 | -9.1389 | 9139.1341 | FALSE | TRUE | TRUE | -30.624
5.1174 | -297.6532 | -9.1151 | 9091.5813 | FALSE | TRUE | TRUE | -30.5442
5.1235 | -296.8645 | -9.091 | 9043.4697 | FALSE | TRUE | TRUE | -30.4633
5.1297 | -296.0647 | -9.0665 | 8994.8065 | FALSE | TRUE | TRUE | -30.3812
5.1358 | -295.2538 | -9.0416 | 8945.5992 | FALSE | TRUE | TRUE | -30.298
5.142 | -294.4317 | -9.0165 | 8895.8551 | FALSE | TRUE | TRUE | -30.2136
5.1481 | -293.5986 | -8.9909 | 8845.5817 | FALSE | TRUE | TRUE | -30.1281
5.1542 | -292.7544 | -8.9651 | 8794.7866 | FALSE | TRUE | TRUE | -30.0415
5.1604 | -291.8992 | -8.9389 | 8743.4774 | FALSE | TRUE | TRUE | -29.9538
5.1665 | -291.033 | -8.9124 | 8691.6619 | FALSE | TRUE | TRUE | -29.8649
5.1726 | -290.1558 | -8.8855 | 8639.3479 | FALSE | TRUE | TRUE | -29.7749
5.1788 | -289.2677 | -8.8583 | 8586.5432 | FALSE | TRUE | TRUE | -29.6837
5.1849 | -288.3687 | -8.8308 | 8533.2558 | FALSE | TRUE | TRUE | -29.5915
5.191 | -287.4589 | -8.8029 | 8479.4937 | FALSE | TRUE | TRUE | -29.4981
5.1972 | -286.5382 | -8.7747 | 8425.2651 | FALSE | TRUE | TRUE | -29.4036
5.2033 | -285.6068 | -8.7462 | 8370.578 | FALSE | TRUE | TRUE | -29.3081
5.2094 | -284.6646 | -8.7174 | 8315.4407 | FALSE | TRUE | TRUE | -29.2114
5.2156 | -283.7116 | -8.6882 | 8259.8616 | FALSE | TRUE | TRUE | -29.1136
5.2217 | -282.748 | -8.6587 | 8203.849 | FALSE | TRUE | TRUE | -29.0147
5.2279 | -281.7738 | -8.6288 | 8147.4113 | FALSE | TRUE | TRUE | -28.9147
5.234 | -280.7889 | -8.5987 | 8090.557 | FALSE | TRUE | TRUE | -28.8137
5.2401 | -279.7935 | -8.5682 | 8033.2947 | FALSE | TRUE | TRUE | -28.7115
5.2463 | -278.7875 | -8.5374 | 7975.6331 | FALSE | TRUE | TRUE | -28.6083
5.2524 | -277.7711 | -8.5063 | 7917.5807 | FALSE | TRUE | TRUE | -28.504
5.2585 | -276.7442 | -8.4748 | 7859.1464 | FALSE | TRUE | TRUE | -28.3986
5.2647 | -275.7068 | -8.443 | 7800.3389 | FALSE | TRUE | TRUE | -28.2922
5.2708 | -274.6591 | -8.411 | 7741.1671 | FALSE | TRUE | TRUE | -28.1846
5.2769 | -273.601 | -8.3786 | 7681.64 | FALSE | TRUE | TRUE | -28.0761
5.2831 | -272.5327 | -8.3458 | 7621.7664 | FALSE | TRUE | TRUE | -27.9664
5.2892 | -271.4541 | -8.3128 | 7561.5554 | FALSE | TRUE | TRUE | -27.8557
5.2954 | -270.3652 | -8.2795 | 7501.016 | FALSE | TRUE | TRUE | -27.744
5.3015 | -269.2662 | -8.2458 | 7440.1575 | FALSE | TRUE | TRUE | -27.6312
5.3076 | -268.157 | -8.2118 | 7378.9888 | FALSE | TRUE | TRUE | -27.5174
5.3138 | -267.0378 | -8.1776 | 7317.5194 | FALSE | TRUE | TRUE | -27.4026
5.3199 | -265.9085 | -8.143 | 7255.7583 | FALSE | TRUE | TRUE | -27.2867
5.326 | -264.7692 | -8.1081 | 7193.7149 | FALSE | TRUE | TRUE | -27.1698
5.3322 | -263.6199 | -8.0729 | 7131.3986 | FALSE | TRUE | TRUE | -27.0518
5.3383 | -262.4606 | -8.0374 | 7068.8188 | FALSE | TRUE | TRUE | -26.9329
5.3444 | -261.2916 | -8.0016 | 7005.9848 | FALSE | TRUE | TRUE | -26.8129
5.3506 | -260.1126 | -7.9655 | 6942.9061 | FALSE | TRUE | TRUE | -26.6919
5.3567 | -258.9239 | -7.9291 | 6879.5923 | FALSE | TRUE | TRUE | -26.5699
5.3628 | -257.7254 | -7.8924 | 6816.0528 | FALSE | TRUE | TRUE | -26.447
5.369 | -256.5172 | -7.8554 | 6752.2973 | FALSE | TRUE | TRUE | -26.323
5.3751 | -255.2994 | -7.8181 | 6688.3353 | FALSE | TRUE | TRUE | -26.198
5.3813 | -254.0719 | -7.7805 | 6624.1764 | FALSE | TRUE | TRUE | -26.072
5.3874 | -252.8349 | -7.7426 | 6559.8304 | FALSE | TRUE | TRUE | -25.9451
5.3935 | -251.5884 | -7.7045 | 6495.3069 | FALSE | TRUE | TRUE | -25.8172
5.3997 | -250.3324 | -7.666 | 6430.6157 | FALSE | TRUE | TRUE | -25.6883
5.4058 | -249.067 | -7.6272 | 6365.7664 | FALSE | TRUE | TRUE | -25.5585
5.4119 | -247.7922 | -7.5882 | 6300.7689 | FALSE | TRUE | TRUE | -25.4276
5.4181 | -246.508 | -7.5489 | 6235.6329 | FALSE | TRUE | TRUE | -25.2959
5.4242 | -245.2146 | -7.5093 | 6170.3682 | FALSE | TRUE | TRUE | -25.1631
5.4303 | -243.9119 | -7.4694 | 6104.9847 | FALSE | TRUE | TRUE | -25.0295
5.4365 | -242.6001 | -7.4292 | 6039.4922 | FALSE | TRUE | TRUE | -24.8948
5.4426 | -241.2791 | -7.3888 | 5973.9006 | FALSE | TRUE | TRUE | -24.7593
5.4488 | -239.9491 | -7.348 | 5908.2198 | FALSE | TRUE | TRUE | -24.6228
5.4549 | -238.61 | -7.307 | 5842.4596 | FALSE | TRUE | TRUE | -24.4854
5.461 | -237.2619 | -7.2657 | 5776.63 | FALSE | TRUE | TRUE | -24.3471
5.4672 | -235.9049 | -7.2242 | 5710.7408 | FALSE | TRUE | TRUE | -24.2078
5.4733 | -234.539 | -7.1823 | 5644.8021 | FALSE | TRUE | TRUE | -24.0676
5.4794 | -233.1643 | -7.1402 | 5578.8236 | FALSE | TRUE | TRUE | -23.9266
5.4856 | -231.7808 | -7.0979 | 5512.8154 | FALSE | TRUE | TRUE | -23.7846
5.4917 | -230.3886 | -7.0552 | 5446.7874 | FALSE | TRUE | TRUE | -23.6417
5.4978 | -228.9877 | -7.0123 | 3775.0084 | FALSE | FALSE | FALSE | -16.4856
5.504 | -227.5782 | -6.9692 | 3728.6778 | FALSE | FALSE | FALSE | -16.3842
5.5101 | -226.1601 | -6.9258 | 3682.3543 | FALSE | FALSE | FALSE | -16.2821
5.5162 | -224.7335 | -6.8821 | 3636.0448 | FALSE | FALSE | FALSE | -16.1794
5.5224 | -223.2984 | -6.8381 | 3589.7563 | FALSE | FALSE | FALSE | -16.076
5.5285 | -221.855 | -6.7939 | 3543.4957 | FALSE | FALSE | FALSE | -15.9721
5.5347 | -220.4031 | -6.7495 | 3497.2701 | FALSE | FALSE | FALSE | -15.8676
5.5408 | -218.943 | -6.7047 | 3451.0863 | FALSE | FALSE | FALSE | -15.7625
5.5469 | -217.4747 | -6.6598 | 3404.9514 | FALSE | FALSE | FALSE | -15.6568
5.5531 | -215.9981 | -6.6146 | 3358.8723 | FALSE | FALSE | FALSE | -15.5505
5.5592 | -214.5134 | -6.5691 | 3312.856 | FALSE | FALSE | FALSE | -15.4436
5.5653 | -213.0207 | -6.5234 | 3266.9093 | FALSE | FALSE | FALSE | -15.3361
5.5715 | -211.5199 | -6.4774 | 3221.0391 | FALSE | FALSE | FALSE | -15.2281
5.5776 | -210.0111 | -6.4312 | 3175.2525 | FALSE | FALSE | FALSE | -15.1194
5.5837 | -208.4945 | -6.3848 | 3129.5562 | FALSE | FALSE | FALSE | -15.0103
5.5899 | -206.97 | -6.3381 | 3083.9572 | FALSE | FALSE | FALSE | -14.9005
5.596 | -205.4377 | -6.2912 | 3038.4624 | FALSE | FALSE | FALSE | -14.7902
5.6022 | -203.8977 | -6.244 | 2993.0785 | FALSE | FALSE | FALSE | -14.6793
5.6083 | -202.35 | -6.1966 | 2947.8124 | FALSE | FALSE | FALSE | -14.5679
5.6144 | -200.7946 | -6.149 | 2902.671 | FALSE | FALSE | FALSE | -14.4559
5.6206 | -199.2318 | -6.1011 | 2857.661 | FALSE | FALSE | FALSE | -14.3434
5.6267 | -197.6614 | -6.053 | 2812.7892 | FALSE | FALSE | FALSE | -14.2303
5.6328 | -196.0835 | -6.0047 | 2768.0624 | FALSE | FALSE | FALSE | -14.1168
5.639 | -194.4983 | -5.9562 | 2723.4873 | FALSE | FALSE | FALSE | -14.0026
5.6451 | -192.9058 | -5.9074 | 2679.0707 | FALSE | FALSE | FALSE | -13.888
5.6512 | -191.306 | -5.8584 | 2634.8191 | FALSE | FALSE | FALSE | -13.7728
5.6574 | -189.699 | -5.8092 | 2590.7393 | FALSE | FALSE | FALSE | -13.6571
5.6635 | -188.0849 | -5.7598 | 2546.8379 | FALSE | FALSE | FALSE | -13.5409
5.6696 | -186.4636 | -5.7101 | 2503.1215 | FALSE | FALSE | FALSE | -13.4242
5.6758 | -184.8354 | -5.6603 | 2459.5968 | FALSE | FALSE | FALSE | -13.307
5.6819 | -183.2002 | -5.6102 | 2416.2702 | FALSE | FALSE | FALSE | -13.1892
5.6881 | -181.5581 | -5.5599 | 2373.1483 | FALSE | FALSE | FALSE | -13.071
5.6942 | -179.9092 | -5.5094 | 2330.2376 | FALSE | FALSE | FALSE | -12.9523
5.7003 | -178.2535 | -5.4587 | 2287.5445 | FALSE | FALSE | FALSE | -12.8331
5.7065 | -176.591 | -5.4078 | 2245.0754 | FALSE | FALSE | FALSE | -12.7134
5.7126 | -174.922 | -5.3567 | 2202.8369 | FALSE | FALSE | FALSE | -12.5933
5.7187 | -173.2463 | -5.3054 | 2160.8352 | FALSE | FALSE | FALSE | -12.4726
5.7249 | -171.5641 | -5.2539 | 2119.0766 | FALSE | FALSE | FALSE | -12.3515
5.731 | -169.8755 | -5.2021 | 2077.5675 | FALSE | FALSE | FALSE | -12.2299
5.7371 | -168.1805 | -5.1502 | 2036.3141 | FALSE | FALSE | FALSE | -12.1079
5.7433 | -166.4791 | -5.0981 | 1995.3225 | FALSE | FALSE | FALSE | -11.9854
5.7494 | -164.7715 | -5.0458 | 1954.5991 | FALSE | FALSE | FALSE | -11.8625
5.7556 | -163.0576 | -4.9934 | 1914.1499 | FALSE | FALSE | FALSE | -11.7391
5.7617 | -161.3377 | -4.9407 | 1873.981 | FALSE | FALSE | FALSE | -11.6153
5.7678 | -159.6116 | -4.8878 | 1834.0984 | FALSE | FALSE | FALSE | -11.491
5.774 | -157.8796 | -4.8348 | 1794.5082 | FALSE | FALSE | FALSE | -11.3663
5.7801 | -156.1416 | -4.7816 | 1755.2163 | FALSE | FALSE | FALSE | -11.2412
5.7862 | -154.3977 | -4.7282 | 1716.2287 | FALSE | FALSE | FALSE | -11.1156
5.7924 | -152.648 | -4.6746 | 1677.5511 | FALSE | FALSE | FALSE | -10.9897
5.7985 | -150.8925 | -4.6208 | 1639.1895 | FALSE | FALSE | FALSE | -10.8633
5.8046 | -149.1314 | -4.5669 | 1601.1497 | FALSE | FALSE | FALSE | -10.7365
5.8108 | -147.3647 | -4.5128 | 1563.4372 | FALSE | FALSE | FALSE | -10.6093
5.8169 | -145.5924 | -4.4585 | 1526.0579 | FALSE | FALSE | FALSE | -10.4817
5.823 | -143.8146 | -4.4041 | 1489.0173 | FALSE | FALSE | FALSE | -10.3537
5.8292 | -142.0315 | -4.3495 | 1452.3211 | FALSE | FALSE | FALSE | -10.2253
5.8353 | -140.2429 | -4.2947 | 1415.9747 | FALSE | FALSE | FALSE | -10.0966
5.8415 | -138.4491 | -4.2398 | 1379.9837 | FALSE | FALSE | FALSE | -9.9674
5.8476 | -136.6501 | -4.1847 | 1344.3534 | FALSE | FALSE | FALSE | -9.8379
5.8537 | -134.8459 | -4.1294 | 1309.0892 | FALSE | FALSE | FALSE | -9.708
5.8599 | -133.0367 | -4.074 | 1274.1964 | FALSE | FALSE | FALSE | -9.5778
5.866 | -131.2224 | -4.0185 | 1239.6804 | FALSE | FALSE | FALSE | -9.4472
5.8721 | -129.4032 | -3.9627 | 1205.5462 | FALSE | FALSE | FALSE | -9.3162
5.8783 | -127.5792 | -3.9069 | 1171.799 | FALSE | FALSE | FALSE | -9.1849
5.8844 | -125.7503 | -3.8509 | 1138.4439 | FALSE | FALSE | FALSE | -9.0532
5.8905 | -123.9167 | -3.7947 | 1105.486 | FALSE | FALSE | FALSE | -8.9212
5.8967 | -122.0784 | -3.7384 | 1072.9301 | FALSE | FALSE | FALSE | -8.7889
5.9028 | -120.2356 | -3.682 | 1040.7812 | FALSE | FALSE | FALSE | -8.6562
5.909 | -118.3882 | -3.6254 | 1009.0442 | FALSE | FALSE | FALSE | -8.5232
5.9151 | -116.5363 | -3.5687 | 977.7238 | FALSE | FALSE | FALSE | -8.3899
5.9212 | -114.6801 | -3.5119 | 946.8247 | FALSE | FALSE | FALSE | -8.2562
5.9274 | -112.8195 | -3.4549 | 916.3516 | FALSE | FALSE | FALSE | -8.1223
5.9335 | -110.9547 | -3.3978 | 886.3091 | FALSE | FALSE | FALSE | -7.988
5.9396 | -109.0857 | -3.3406 | 856.7016 | FALSE | FALSE | FALSE | -7.8535
5.9458 | -107.2127 | -3.2832 | 827.5337 | FALSE | FALSE | FALSE | -7.7186
5.9519 | -105.3355 | -3.2257 | 798.8098 | FALSE | FALSE | FALSE | -7.5835
5.958 | -103.4544 | -3.1681 | 770.5342 | FALSE | FALSE | FALSE | -7.4481
5.9642 | -101.5695 | -3.1104 | 742.711 | FALSE | FALSE | FALSE | -7.3123
5.9703 | -99.6807 | -3.0525 | 715.3446 | FALSE | FALSE | FALSE | -7.1764
5.9764 | -97.7881 | -2.9946 | 688.4391 | FALSE | FALSE | FALSE | -7.0401
5.9826 | -95.8918 | -2.9365 | 661.9984 | FALSE | FALSE | FALSE | -6.9036
5.9887 | -93.992 | -2.8783 | 636.0266 | FALSE | FALSE | FALSE | -6.7668
5.9949 | -92.0886 | -2.8201 | 610.5276 | FALSE | FALSE | FALSE | -6.6298
6.001 | -90.1817 | -2.7617 | 585.5053 | FALSE | FALSE | FALSE | -6.4925
6.0071 | -88.2715 | -2.7032 | 560.9633 | FALSE | FALSE | FALSE | -6.355
6.0133 | -86.3579 | -2.6446 | 536.9054 | FALSE | FALSE | FALSE | -6.2172
6.0194 | -84.4411 | -2.5859 | 513.3353 | FALSE | FALSE | FALSE | -6.0792
6.0255 | -82.5211 | -2.5271 | 490.2564 | FALSE | FALSE | FALSE | -5.941
6.0317 | -80.598 | -2.4682 | 467.6722 | FALSE | FALSE | FALSE | -5.8025
6.0378 | -78.6718 | -2.4092 | 445.5862 | FALSE | FALSE | FALSE | -5.6639
6.0439 | -76.7427 | -2.3501 | 424.0017 | FALSE | FALSE | FALSE | -5.525
6.0501 | -74.8107 | -2.2909 | 402.9219 | FALSE | FALSE | FALSE | -5.3859
6.0562 | -72.8759 | -2.2317 | 382.35 | FALSE | FALSE | FALSE | -5.2466
6.0624 | -70.9383 | -2.1724 | 362.289 | FALSE | FALSE | FALSE | -5.1071
6.0685 | -68.9981 | -2.1129 | 342.7421 | FALSE | FALSE | FALSE | -4.9674
6.0746 | -67.0552 | -2.0534 | 323.7122 | FALSE | FALSE | FALSE | -4.8275
6.0808 | -65.1099 | -1.9939 | 305.202 | FALSE | FALSE | FALSE | -4.6875
6.0869 | -63.1621 | -1.9342 | 287.2145 | FALSE | FALSE | FALSE | -4.5473
6.093 | -61.2119 | -1.8745 | 269.7523 | FALSE | FALSE | FALSE | -4.4069
6.0992 | -59.2594 | -1.8147 | 252.8181 | FALSE | FALSE | FALSE | -4.2663
6.1053 | -57.3047 | -1.7549 | 236.4143 | FALSE | FALSE | FALSE | -4.1256
6.1114 | -55.3478 | -1.6949 | 220.5435 | FALSE | FALSE | FALSE | -3.9847
6.1176 | -53.3888 | -1.6349 | 205.2081 | FALSE | FALSE | FALSE | -3.8437
6.1237 | -51.4279 | -1.5749 | 190.4104 | FALSE | FALSE | FALSE | -3.7025
6.1298 | -49.465 | -1.5148 | 176.1525 | FALSE | FALSE | FALSE | -3.5612
6.136 | -47.5002 | -1.4546 | 162.4367 | FALSE | FALSE | FALSE | -3.4197
6.1421 | -45.5336 | -1.3944 | 149.265 | FALSE | FALSE | FALSE | -3.2781
6.1483 | -43.5654 | -1.3341 | 136.6394 | FALSE | FALSE | FALSE | -3.1364
6.1544 | -41.5954 | -1.2738 | 124.5618 | FALSE | FALSE | FALSE | -2.9946
6.1605 | -39.624 | -1.2134 | 113.0341 | FALSE | FALSE | FALSE | -2.8527
6.1667 | -37.651 | -1.153 | 102.0578 | FALSE | FALSE | FALSE | -2.7106
6.1728 | -35.6766 | -1.0925 | 91.6348 | FALSE | FALSE | FALSE | -2.5685
6.1789 | -33.7009 | -1.032 | 81.7666 | FALSE | FALSE | FALSE | -2.4262
6.1851 | -31.7239 | -0.97149 | 72.4546 | FALSE | FALSE | FALSE | -2.2839
6.1912 | -29.7457 | -0.91091 | 63.7002 | FALSE | FALSE | FALSE | -2.1415
6.1973 | -27.7664 | -0.8503 | 55.5049 | FALSE | FALSE | FALSE | -1.999
6.2035 | -25.786 | -0.78965 | 47.8698 | FALSE | FALSE | FALSE | -1.8564
6.2096 | -23.8047 | -0.72898 | 40.796 | FALSE | FALSE | FALSE | -1.7138
6.2158 | -21.8224 | -0.66827 | 34.2847 | FALSE | FALSE | FALSE | -1.5711
6.2219 | -19.8394 | -0.60755 | 28.3367 | FALSE | FALSE | FALSE | -1.4283
6.228 | -17.8556 | -0.5468 | 22.9531 | FALSE | FALSE | FALSE | -1.2855
6.2342 | -15.8711 | -0.48603 | 18.1346 | FALSE | FALSE | FALSE | -1.1426
6.2403 | -13.886 | -0.42524 | 13.882 | FALSE | FALSE | FALSE | -0.99971
6.2464 | -11.9005 | -0.36443 | 10.1958 | FALSE | FALSE | FALSE | -0.85676
6.2526 | -9.9144 | -0.30361 | 7.0767 | FALSE | FALSE | FALSE | -0.71377
6.2587 | -7.928 | -0.24278 | 4.525 | FALSE | FALSE | FALSE | -0.57077
6.2648 | -5.9413 | -0.18194 | 2.5413 | FALSE | FALSE | FALSE | -0.42774
6.271 | -3.9544 | -0.1211 | 1.1258 | FALSE | FALSE | FALSE | -0.28469
6.2771 | -1.9673 | -0.060245 | 0.27863 | FALSE | FALSE | FALSE | -0.14163
6.2832 | 0.019872 | 0.00060854 | 2.8429e-05 | FALSE | FALSE | FALSE | 0.0014306
2

## Class-A
Class-A evaluation |  | THC-I | POHC
|  | 1.0894 | 0.20427
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
| Harm no. | Amplitude | Tolerance |  |  |  | of Limit
| 1 | 2.3534 |  |  | Limit | Status | %
| 2 | 3.97e-05 | 0 | 0.012844 | 1.08 | PASS | 0
| 3 | 0.91499 | 0.86924 | 0.95845 | 2.3 | PASS | 39.782
| 4 | 1.2067e-07 | 0 | 0.012804 | 0.43 | PASS | 0
| 5 | 0.30503 | 0.28978 | 0.31952 | 1.14 | PASS | 26.7569
| 6 | 3.9702e-05 | 0 | 0.012844 | 0.3 | PASS | 0
| 7 | 0.305 | 0.28975 | 0.31949 | 0.77 | PASS | 39.6105
| 8 | 1.2057e-07 | 0 | 0.012804 | 0.23 | PASS | 0
| 9 | 0.18304 | 0.17024 | 0.19585 | 0.4 | PASS | 45.7604
| 10 | 3.9706e-05 | 0 | 0.012844 | 0.184 | PASS | 0
| 11 | 0.18301 | 0.17021 | 0.19582 | 0.33 | PASS | 55.4586
| 12 | 1.2079e-07 | 0 | 0.012804 | 0.153 | PASS | 0
| 13 | 0.13077 | 0.11796 | 0.14357 | 0.21 | PASS | 62.2703
| 14 | 3.9711e-05 | 0 | 0.012844 | 0.13143 | PASS | 0
| 15 | 0.13074 | 0.11794 | 0.14354 | 0.15 | PASS | 87.1597
| 16 | 1.2076e-07 | 0 | 0.012804 | 0.115 | PASS | 0
| 17 | 0.10173 | 0.088928 | 0.11454 | 0.13235 | PASS | 76.864
| 18 | 3.9719e-05 | 0 | 0.012844 | 0.10222 | PASS | 0
| 19 | 0.1017 | 0.088899 | 0.11451 | 0.11842 | PASS | 85.8831
| 20 | 1.2103e-07 | 0 | 0.012804 | 0.092 | PASS | 0
| 21 | 0.083258 | 0.070454 | 0.096063 | 0.10714 | PASS | 77.7079
| 22 | 3.9729e-05 | 0 | 0.012844 | 0.083636 | PASS | 0
| 23 | 0.08323 | 0.070426 | 0.096035 | 0.097826 | PASS | 85.08
| 24 | 1.2106e-07 | 0 | 0.012804 | 0.076667 | PASS | 0
| 25 | 0.070473 | 0.057669 | 0.083277 | 0.09 | PASS | 78.3032
| 26 | 3.9741e-05 | 0 | 0.012844 | 0.070769 | PASS | 0
| 27 | 0.070445 | 0.057641 | 0.083249 | 0.083333 | PASS | 84.5337
| 28 | 1.214e-07 | 0 | 0.012804 | 0.065714 | PASS | 0
| 29 | 0.0611 | 0.048296 | 0.073904 | 0.077586 | PASS | 78.7509
| 30 | 3.9755e-05 | 0 | 0.012844 | 0.061333 | PASS | 0
| 31 | 0.061072 | 0.048268 | 0.073876 | 0.072581 | PASS | 84.1433
| 32 | 1.2149e-07 | 0 | 0.012804 | 0.0575 | PASS | 0
| 33 | 0.053935 | 0.041131 | 0.066739 | 0.068182 | PASS | 79.1046
| 34 | 3.9771e-05 | 0 | 0.012844 | 0.054118 | PASS | 0
| 35 | 0.053907 | 0.041103 | 0.066711 | 0.064286 | PASS | 83.8551
| 36 | 1.2188e-07 | 0 | 0.012804 | 0.051111 | PASS | 0
| 37 | 0.048281 | 0.035477 | 0.061085 | 0.060811 | PASS | 79.3952
| 38 | 3.9789e-05 | 0 | 0.012844 | 0.048421 | PASS | 0
| 39 | 0.048253 | 0.035449 | 0.061057 | 0.057692 | PASS | 83.6381
| 40 | 1.2203e-07 | 0 | 0.012804 | 0.046 | PASS | 0

## Class-B
Class-B evaluation |  | THC-I | POHC
|  | 1.0894 | 0.20427
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
|  |  | Tolerance |  |  |  | of Limit
| 1 | 2.3534
| 2 | 0 | 0 | 0.012844 | 1.62 | PASS | 0
| 3 | 0.91499 | 0.86924 | 0.95845 | 3.45 | PASS | 26.5213
| 4 | 0 | 0 | 0.012804 | 0.645 | PASS | 0
| 5 | 0.30503 | 0.28978 | 0.31952 | 1.71 | PASS | 17.838
| 6 | 0 | 0 | 0.012844 | 0.45 | PASS | 0
| 7 | 0.305 | 0.28975 | 0.31949 | 1.155 | PASS | 26.407
| 8 | 0 | 0 | 0.012804 | 0.345 | PASS | 0
| 9 | 0.18304 | 0.17024 | 0.19585 | 0.6 | PASS | 30.5069
| 10 | 0 | 0 | 0.012844 | 0.276 | PASS | 0
| 11 | 0.18301 | 0.17021 | 0.19582 | 0.495 | PASS | 36.9724
| 12 | 0 | 0 | 0.012804 | 0.2295 | PASS | 0
| 13 | 0.13077 | 0.11796 | 0.14357 | 0.315 | PASS | 41.5135
| 14 | 0 | 0 | 0.012844 | 0.19714 | PASS | 0
| 15 | 0.13074 | 0.11794 | 0.14354 | 0.225 | PASS | 58.1065
| 16 | 0 | 0 | 0.012804 | 0.1725 | PASS | 0
| 17 | 0.10173 | 0.088928 | 0.11454 | 0.19853 | PASS | 51.2426
| 18 | 0 | 0 | 0.012844 | 0.15333 | PASS | 0
| 19 | 0.1017 | 0.088899 | 0.11451 | 0.17763 | PASS | 57.2554
| 20 | 0 | 0 | 0.012804 | 0.138 | PASS | 0
| 21 | 0.083258 | 0.070454 | 0.096063 | 0.16071 | PASS | 51.8053
| 22 | 0 | 0 | 0.012844 | 0.12545 | PASS | 0
| 23 | 0.08323 | 0.070426 | 0.096035 | 0.14674 | PASS | 56.72
| 24 | 0 | 0 | 0.012804 | 0.115 | PASS | 0
| 25 | 0.070473 | 0.057669 | 0.083277 | 0.135 | PASS | 52.2021
| 26 | 0 | 0 | 0.012844 | 0.10615 | PASS | 0
| 27 | 0.070445 | 0.057641 | 0.083249 | 0.125 | PASS | 56.3558
| 28 | 0 | 0 | 0.012804 | 0.098571 | PASS | 0
| 29 | 0.0611 | 0.048296 | 0.073904 | 0.11638 | PASS | 52.5006
| 30 | 0 | 0 | 0.012844 | 0.092 | PASS | 0
| 31 | 0.061072 | 0.048268 | 0.073876 | 0.10887 | PASS | 56.0955
| 32 | 0 | 0 | 0.012804 | 0.08625 | PASS | 0
| 33 | 0.053935 | 0.041131 | 0.066739 | 0.10227 | PASS | 52.7364
| 34 | 0 | 0 | 0.012844 | 0.081176 | PASS | 0
| 35 | 0.053907 | 0.041103 | 0.066711 | 0.096429 | PASS | 55.9034
| 36 | 0 | 0 | 0.012804 | 0.076667 | PASS | 0
| 37 | 0.048281 | 0.035477 | 0.061085 | 0.091216 | PASS | 52.9302
| 38 | 0 | 0 | 0.012844 | 0.072632 | PASS | 0
| 39 | 0.048253 | 0.035449 | 0.061057 | 0.086538 | PASS | 55.7587
| 40 | 0 | 0 | 0.012804 | 0.069 | PASS | 0

## Class-C
Class-C evaluation |  | THC-I | POHC
|  | 1.0894 | 0.20427
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
| Harm no. | Amplitude | Tolerance |  |  |  | of Limit
| 1 | 2.3534
| 2 | 3.97e-05 | 0 | 0.012844 | 0.047068 | PASS | 0
| 3 | 0.91499 | 0.86924 | 0.95845 | 0.63873 | Fail | 143.2503
| 4 | 1.2067e-07 | 0 | 0.012804 | n/l | PASS | 0
| 5 | 0.30503 | 0.28978 | 0.31952 | 0.23534 | Fail | 129.6109
| 6 | 3.9702e-05 | 0 | 0.012844 | n/l | PASS | 0
| 7 | 0.305 | 0.28975 | 0.31949 | 0.16474 | Fail | 185.1414
| 8 | 1.2057e-07 | 0 | 0.012804 | n/l | PASS | 0
| 9 | 0.18304 | 0.17024 | 0.19585 | 0.11767 | Fail | 155.5535
| 10 | 3.9706e-05 | 0 | 0.012844 | n/l | PASS | 0
| 11 | 0.18301 | 0.17021 | 0.19582 | 0.070603 | Fail | 259.216
| 12 | 1.2079e-07 | 0 | 0.012804 | n/l | PASS | 0
| 13 | 0.13077 | 0.11796 | 0.14357 | 0.070603 | Fail | 185.2163
| 14 | 3.9711e-05 | 0 | 0.012844 | n/l | PASS | 0
| 15 | 0.13074 | 0.11794 | 0.14354 | 0.070603 | Fail | 185.1765
| 16 | 1.2076e-07 | 0 | 0.012804 | n/l | PASS | 0
| 17 | 0.10173 | 0.088928 | 0.11454 | 0.070603 | Fail | 144.0905
| 18 | 3.9719e-05 | 0 | 0.012844 | n/l | PASS | 0
| 19 | 0.1017 | 0.088899 | 0.11451 | 0.070603 | Fail | 144.0507
| 20 | 1.2103e-07 | 0 | 0.012804 | n/l | PASS | 0
| 21 | 0.083258 | 0.070454 | 0.096063 | 0.070603 | Fail | 117.9254
| 22 | 3.9729e-05 | 0 | 0.012844 | n/l | PASS | 0
| 23 | 0.08323 | 0.070426 | 0.096035 | 0.070603 | Fail | 117.8856
| 24 | 1.2106e-07 | 0 | 0.012804 | n/l | PASS | 0
| 25 | 0.070473 | 0.057669 | 0.083277 | 0.070603 | PASS | 99.8162
| 26 | 3.9741e-05 | 0 | 0.012844 | n/l | PASS | 0
| 27 | 0.070445 | 0.057641 | 0.083249 | 0.070603 | PASS | 99.7764
| 28 | 1.214e-07 | 0 | 0.012804 | n/l | PASS | 0
| 29 | 0.0611 | 0.048296 | 0.073904 | 0.070603 | PASS | 86.5404
| 30 | 3.9755e-05 | 0 | 0.012844 | n/l | PASS | 0
| 31 | 0.061072 | 0.048268 | 0.073876 | 0.070603 | PASS | 86.5006
| 32 | 1.2149e-07 | 0 | 0.012804 | n/l | PASS | 0
| 33 | 0.053935 | 0.041131 | 0.066739 | 0.070603 | PASS | 76.3922
| 34 | 3.9771e-05 | 0 | 0.012844 | n/l | PASS | 0
| 35 | 0.053907 | 0.041103 | 0.066711 | 0.070603 | PASS | 76.3524
| 36 | 1.2188e-07 | 0 | 0.012804 | n/l | PASS | 0
| 37 | 0.048281 | 0.035477 | 0.061085 | 0.070603 | PASS | 68.3839
| 38 | 3.9789e-05 | 0 | 0.012844 | n/l | PASS | 0
| 39 | 0.048253 | 0.035449 | 0.061057 | 0.070603 | PASS | 68.3441
| 40 | 1.2203e-07 | 0 | 0.012804 | n/l | PASS | 0

## Class-D
Class-D evaluation |  | THC-I | POHC
|  | 1.0894 | 0.20427
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
|  |  | Tolerance |  |  |  | of Limit
| 1 | 2.3534
| 2 | 3.97e-05 | 0 | 0.012844 | N/A | PASS | 0
| 3 | 0.91499 | 0.86924 | 0.95845 | 1.8404 | PASS | 49.7174
| 4 | 1.2067e-07 | 0 | 0.012804 | N/A | PASS | 0
| 5 | 0.30503 | 0.28978 | 0.31952 | 1.0284 | PASS | 29.6593
| 6 | 3.9702e-05 | 0 | 0.012844 | N/A | PASS | 0
| 7 | 0.305 | 0.28975 | 0.31949 | 0.54129 | PASS | 56.3475
| 8 | 1.2057e-07 | 0 | 0.012804 | N/A | PASS | 0
| 9 | 0.18304 | 0.17024 | 0.19585 | 0.27064 | PASS | 67.6321
| 10 | 3.9706e-05 | 0 | 0.012844 | N/A | PASS | 0
| 11 | 0.18301 | 0.17021 | 0.19582 | 0.18945 | PASS | 96.6025
| 12 | 1.2079e-07 | 0 | 0.012804 | N/A | PASS | 0
| 13 | 0.13077 | 0.11796 | 0.14357 | 0.16022 | PASS | 81.6173
| 14 | 3.9711e-05 | 0 | 0.012844 | N/A | PASS | 0
| 15 | 0.13074 | 0.11794 | 0.14354 | 0.13893 | PASS | 94.1046
| 16 | 1.2076e-07 | 0 | 0.012804 | N/A | PASS | 0
| 17 | 0.10173 | 0.088928 | 0.11454 | 0.12259 | PASS | 82.9885
| 18 | 3.9719e-05 | 0 | 0.012844 | N/A | PASS | 0
| 19 | 0.1017 | 0.088899 | 0.11451 | 0.10968 | PASS | 92.7263
| 20 | 1.2103e-07 | 0 | 0.012804 | N/A | PASS | 0
| 21 | 0.083258 | 0.070454 | 0.096063 | 0.099236 | PASS | 83.8997
| 22 | 3.9729e-05 | 0 | 0.012844 | N/A | PASS | 0
| 23 | 0.08323 | 0.070426 | 0.096035 | 0.090606 | PASS | 91.8592
| 24 | 1.2106e-07 | 0 | 0.012804 | N/A | PASS | 0
| 25 | 0.070473 | 0.057669 | 0.083277 | 0.083358 | PASS | 84.5424
| 26 | 3.9741e-05 | 0 | 0.012844 | N/A | PASS | 0
| 27 | 0.070445 | 0.057641 | 0.083249 | 0.077183 | PASS | 91.2694
| 28 | 1.214e-07 | 0 | 0.012804 | N/A | PASS | 0
| 29 | 0.0611 | 0.048296 | 0.073904 | 0.07186 | PASS | 85.0258
| 30 | 3.9755e-05 | 0 | 0.012844 | N/A | PASS | 0
| 31 | 0.061072 | 0.048268 | 0.073876 | 0.067224 | PASS | 90.8479
| 32 | 1.2149e-07 | 0 | 0.012804 | N/A | PASS | 0
| 33 | 0.053935 | 0.041131 | 0.066739 | 0.06315 | PASS | 85.4077
| 34 | 3.9771e-05 | 0 | 0.012844 | N/A | PASS | 0
| 35 | 0.053907 | 0.041103 | 0.066711 | 0.059541 | PASS | 90.5367
| 36 | 1.2188e-07 | 0 | 0.012804 | N/A | PASS | 0
| 37 | 0.048281 | 0.035477 | 0.061085 | 0.056323 | PASS | 85.7215
| 38 | 3.9789e-05 | 0 | 0.012844 | N/A | PASS | 0
| 39 | 0.048253 | 0.035449 | 0.061057 | 0.053435 | PASS | 90.3024
| 40 | 1.2203e-07 | 0 | 0.012804 | N/A | PASS | 0

## Table-2
Table-2 Evaluation
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
| 1 | 22.2249 | Tolerance |  |  |  | of Limit
| 3 | 2.2322 | 2.1206 | 2.3382 | 4.836 | PASS | 46.1575
| 5 | 0.74414 | 0.70693 | 0.77949 | 2.3956 | PASS | 31.0627
| 7 | 0.74407 | 0.70687 | 0.77942 | 1.612 | PASS | 46.1584
| 9 | 0.44654 | 0.42422 | 0.46775 | 0.85078 | PASS | 52.4865
| 11 | 0.44648 | 0.42415 | 0.46768 | 0.69406 | PASS | 64.3285
| 13 | 0.31902 | 0.30307 | 0.33417 | 0.44778 | PASS | 71.2446
| 15 | 0.31895 | 0.303 | 0.3341
| 17 | 0.24818 | 0.23577 | 0.25997
| 19 | 0.24811 | 0.23571 | 0.2599
| 21 | 0.20312 | 0.19296 | 0.21276
| 23 | 0.20305 | 0.19289 | 0.21269
| 25 | 0.17192 | 0.16333 | 0.18009
| 27 | 0.17186 | 0.16326 | 0.18002
| 29 | 0.14906 | 0.1416 | 0.15614
| 31 | 0.14899 | 0.14154 | 0.15607
| 33 | 0.13158 | 0.125 | 0.13783
| 35 | 0.13151 | 0.12493 | 0.13776
| 37 | 0.11778 | 0.1119 | 0.12338
| 39 | 0.11772 | 0.11183 | 0.12331
| THC-I | PWHC
| 11.8709 | 14.5806
THC & PWHC Limits
| 23 | 23

## Table-3
Table-3 Evaluation
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
| 1 | 22.2249 | Tolerance |  |  |  | of Limit
| 3 | 2.2322 | 2.1206 | 2.3382 | 7.1868 | PASS | 31.0593
| 5 | 0.74414 | 0.70693 | 0.77949 | 2.3956 | PASS | 31.0627
| 7 | 0.74407 | 0.70687 | 0.77942 | 1.612 | PASS | 46.1584
| 9 | 0.44654 | 0.42422 | 0.46775 | 0.69406 | PASS | 64.3383
| 11 | 0.44648 | 0.42415 | 0.46768 | 0.69406 | PASS | 64.3285
| 13 | 0.31902 | 0.30307 | 0.33417 | 0.44778 | PASS | 71.2446
| 15 | 0.31895 | 0.303 | 0.3341
| 17 | 0.24818 | 0.23577 | 0.25997
| 19 | 0.24811 | 0.23571 | 0.2599
| 21 | 0.20312 | 0.19296 | 0.21276
| 23 | 0.20305 | 0.19289 | 0.21269
| 25 | 0.17192 | 0.16333 | 0.18009
| 27 | 0.17186 | 0.16326 | 0.18002
| 29 | 0.14906 | 0.1416 | 0.15614
| 31 | 0.14899 | 0.14154 | 0.15607
| 33 | 0.13158 | 0.125 | 0.13783
| 35 | 0.13151 | 0.12493 | 0.13776
| 37 | 0.11778 | 0.1119 | 0.12338
| 39 | 0.11772 | 0.11183 | 0.12331
| THC-I | PWHC
| 11.8709 | 14.5806
THC & PWHC Limits
| 13 | 22

## Table-4
Table-4 Evaluation
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
| 1 | 22.2249 | Tolerance |  |  |  | of Limit
| 3 | 2.2322 | 2.1206 | 2.3382 | 7.1868 | PASS | 31.0593
| 5 | 0.74414 | 0.70693 | 0.77949 | 2.3956 | PASS | 31.0627
| 7 | 0.74407 | 0.70687 | 0.77942 | 1.612 | PASS | 46.1584
| 9 | 0.44654 | 0.42422 | 0.46775 | 0.69406 | PASS | 64.3383
| 11 | 0.44648 | 0.42415 | 0.46768 | 0.69406 | PASS | 64.3285
| 13 | 0.31902 | 0.30307 | 0.33417 | 0.44778 | PASS | 71.2446
| 15 | 0.31895 | 0.303 | 0.3341
| 17 | 0.24818 | 0.23577 | 0.25997
| 19 | 0.24811 | 0.23571 | 0.2599
| 21 | 0.20312 | 0.19296 | 0.21276
| 23 | 0.20305 | 0.19289 | 0.21269
| 25 | 0.17192 | 0.16333 | 0.18009
| 27 | 0.17186 | 0.16326 | 0.18002
| 29 | 0.14906 | 0.1416 | 0.15614
| 31 | 0.14899 | 0.14154 | 0.15607
| 33 | 0.13158 | 0.125 | 0.13783
| 35 | 0.13151 | 0.12493 | 0.13776
| 37 | 0.11778 | 0.1119 | 0.12338
| 39 | 0.11772 | 0.11183 | 0.12331
| THC-I | PWHC
| 11.8709 | 14.5806
THC & PWHC Limits
| 13 | 48

## Table-5
Table-5 Evaluation
| Harm . No. | Ideal | Min | Max | Limits | Pass/Fail | Percent
| 1 | 22.2249 | Tolerance |  |  |  | of Limit
| 3 | 2.2322 | 2.1206 | 2.3382 | 7.1868 | PASS | 31.0593
| 5 | 0.74414 | 0.70693 | 0.77949 | 2.3956 | PASS | 31.0627
| 7 | 0.74407 | 0.70687 | 0.77942 | 1.612 | PASS | 46.1584
| 9 | 0.44654 | 0.42422 | 0.46775 | 0.69406 | PASS | 64.3383
| 11 | 0.44648 | 0.42415 | 0.46768 | 0.69406 | PASS | 64.3285
| 13 | 0.31902 | 0.30307 | 0.33417 | 0.44778 | PASS | 71.2446
| 15 | 0.31895 | 0.303 | 0.3341 | 100 | PASS | 0.31895
| 17 | 0.24818 | 0.23577 | 0.25997 | 0.44778 | PASS | 55.4253
| 19 | 0.24811 | 0.23571 | 0.2599 | 0.33583 | PASS | 73.88
| 21 | 0.20312 | 0.19296 | 0.21276 | 100 | PASS | 0.20312
| 23 | 0.20305 | 0.19289 | 0.21269 | 0.33583 | PASS | 60.4606
| 25 | 0.17192 | 0.16333 | 0.18009 | 0.33583 | PASS | 51.1933
| 27 | 0.17186 | 0.16326 | 0.18002 | 100 | PASS | 0.17186
| 29 | 0.14906 | 0.1416 | 0.15614 | 0.22389 | PASS | 66.5766
| 31 | 0.14899 | 0.14154 | 0.15607 | 0.22389 | PASS | 66.5461
| 33 | 0.13158 | 0.125 | 0.13783 | 100 | PASS | 0.13158
| 35 | 0.13151 | 0.12493 | 0.13776 | 0.22389 | PASS | 58.7388
| 37 | 0.11778 | 0.1119 | 0.12338 | 0.22389 | PASS | 52.6086
| 39 | 0.11772 | 0.11183 | 0.12331 | 100 | PASS | 0.11772
| THC-I | PWHC
| 11.8709 | 14.5806
THC & PWHC Limits
| 13 | 48